## RB kW Offset Wksht
Axiom Exergy - Refrigeration Battery kW Offset Calculation Worksheet
Note: Green Cell = data input field | [5 empty] | Total Offset kW | #DIV/0!
Note: Yellow Cell = Final Product
Step 1: Data Inputs | [5 empty] | Step 2: Outputs for SGIP Calculations
Compressors
| Suction Group 1 | Suction Group 2 | Suction Group 3 | Suction Group 4 | Data Source
Refrigerant Type |  |  |  |  | Field observation | 1) Weighted Average Compressor Lift during On-Peak Hours of a Peak Day (deg F) | #DIV/0!
Average Saturated Suction Temperature during On-Peak Hours of a Peak Day (deg F) |  |  |  |  | Setpoint read from RMCS | 2) Average Compressor EER during On-Peak Hours of a Peak Day (BTUh/W) | #DIV/0!
Average Saturated Condensing Temp during On-Peak Hours of a Peak Day (deg F) |  |  |  |  | Setpoint and/or trend data read from RMCS (or historical weather data) | 3) Cumulative Rated Suction Group Capacity (without subcooling) (BTUh) | 0
Rated Suction Group Capacity (without subcooling) (BTUh) |  |  |  |  | Refrigeration schedule/drawing or manufacturer data sheets, calculated if not defined for current operational setpoints | 4) Weighted Average of the Maximum Recorded Output during On-Peak Hours (% of Rated Suction Group Capacity) | #DIV/0!
Suction Group Maximum Recorded Output during On-Peak Hours (% of Rated Suction Group Capacity) |  |  |  |  | Historical data read from RMCS or loggers placed during site visits | 5) Compressor kW Offset | #DIV/0!
Notes:
-Only fill out columns for suction groups that the Refrigeration Battery is connected to.
-A "Peak Day" is defined as the day of any chosen summer month (as defined by the facility's electricity rate schedule) in the last 12 months with the highest average ambient dry-bulb air temperature (as recorded in historical weather data) during summer "On-Peak" hours (as defined by the facility's electricity rate schedule).
-The Saturated Condensing Temperature is either a fixed setpoint or it "floats" at 8, 10, 15, or 20 degrees F higher than the ambient air temperature (this setpoint can be found in the RMCS or refrigeration schedule/drawing).
-"Suction Group Maximum Recorded Output during On-Peak Hours" is defined as the maximum recorded compressor output (as a % of the rated suction group output) at any point during summer "On-Peak" hours (as defined by the facility's electricity rate schedule) in the last 12 months according to available data.
-Compressor "Lift" is defined as Saturated Condensing Temperature minus Saturated Suction Temperature.
Condensers
| Suction Group 1 | Suction Group 2 | Suction Group 3 | Suction Group 4 | Data Source
Number of Condenser fans |  |  |  |  | Field observation | 1) Cumulative Number of Condenser Fans | 0
Measured Condenser Fan Power (W/fan) |  |  |  |  | Field measurement (or VFD readout, if applicable) | 2) Weighted Average Condenser Fan Power (W/fan) | #DIV/0!
Condenser Fan Group Maximum Recorded Output during On-Peak Hours (% of Rated Fan Group Capacity) |  |  |  |  | Historical data read from RMCS or loggers placed during site visits | 3) Weighted Average of the Maximum Recorded Output during On-Peak Hours (% of Rated Fan Group Capacity) | #DIV/0!
[6 empty] | 4) Condenser kW Offset | #DIV/0!
Notes:
- Only fill out columns for suction groups that the Refrigeration Battery is connected to. If two or more suction groups share condenser fans, only enter condenser fans once.
-"Condenser Fan Group Maximum Recorded Output during On-Peak Hours" is defined as the maximum recorded condenser output (as a % of the rated condenser fan group capacity) at any point during summer "On-Peak" hours (as defined by the facility's electricity rate schedule) in the last 12 months according to available data.
Parasitic Losses
Parasitic Load during Discharge (kW)
Notes:
-Parasitic losses during discharge are specified by the manfucturer.

## 404a Compressor EER vs Lift
404a Compressor EER vs. Lift Curve | [8 empty] | Example compressor data sheet (source of data in table):
Data source: manufacturer data sheets from Copeland, IR, Carlyle, Bitzer | [6 empty] | Empirical Compressor Performance Equation
Analysis based on ~54 compressors types found in 38 compressor racks | [6 empty] | Calculate EER (y) from Lift (x):
Manufacturer | Model # | HP | SCT (F) | SST (F) | Lift (F) | EER | y = (c3 * x^3) + (c2 * x^2) + (c1 * x) + b
Carlyle | 06EM450 | 15 | 110 | 10 | 100 | 7.6
Carlyle | 06EM450 | 15 | 110 | 15 | 95 | 8.1 | c3 | -1.7576e-05
Carlyle | 06EM450 | 15 | 110 | 20 | 90 | 8.7 | c2 | 0.0064209
Carlyle | 06EM450 | 15 | 110 | 25 | 85 | 9.3 | c1 | -0.86081
Carlyle | 06EM450 | 15 | 110 | 30 | 80 | 10 | b | 47.249
Carlyle | 06EM450 | 15 | 110 | 35 | 75 | 10.7
Carlyle | 06EM450 | 15 | 100 | 10 | 90 | 8.9
Carlyle | 06EM450 | 15 | 100 | 15 | 85 | 9.5
Carlyle | 06EM450 | 15 | 100 | 20 | 80 | 10.3
Carlyle | 06EM450 | 15 | 100 | 25 | 75 | 11.1
Carlyle | 06EM450 | 15 | 100 | 30 | 70 | 12
Carlyle | 06EM450 | 15 | 100 | 35 | 65 | 12.9
Carlyle | 06EM450 | 15 | 90 | 10 | 80 | 10.5
Carlyle | 06EM450 | 15 | 90 | 15 | 75 | 11.3
Carlyle | 06EM450 | 15 | 90 | 20 | 70 | 12.3
Carlyle | 06EM450 | 15 | 90 | 25 | 65 | 13.3
Carlyle | 06EM450 | 15 | 90 | 30 | 60 | 14.4
Carlyle | 06EM450 | 15 | 90 | 35 | 55 | 15.7
Carlyle | 06EM450 | 15 | 80 | 10 | 70 | 12.4
Carlyle | 06EM450 | 15 | 80 | 15 | 65 | 13.5
Carlyle | 06EM450 | 15 | 80 | 20 | 60 | 14.7
Carlyle | 06EM450 | 15 | 80 | 25 | 55 | 16
Carlyle | 06EM450 | 15 | 80 | 30 | 50 | 17.6
Carlyle | 06EM450 | 15 | 80 | 35 | 45 | 19.3
Carlyle | 06EM450 | 15 | 70 | 10 | 60 | 14.6
Carlyle | 06EM450 | 15 | 70 | 15 | 55 | 16
Carlyle | 06EM450 | 15 | 70 | 20 | 50 | 17.6
Carlyle | 06EM450 | 15 | 70 | 25 | 45 | 19.4
Carlyle | 06EM450 | 15 | 70 | 30 | 40 | 21.5
Carlyle | 06EM450 | 15 | 70 | 35 | 35 | 23.9
Carlyle | 06EA565 | 25 | 110 | 10 | 100 | 7.7
Carlyle | 06EA565 | 25 | 110 | 15 | 95 | 8.2
Carlyle | 06EA565 | 25 | 110 | 20 | 90 | 8.8
Carlyle | 06EA565 | 25 | 110 | 25 | 85 | 9.4
Carlyle | 06EA565 | 25 | 110 | 30 | 80 | 10.1
Carlyle | 06EA565 | 25 | 110 | 35 | 75 | 10.9
Carlyle | 06EA565 | 25 | 100 | 10 | 90 | 8.9
Carlyle | 06EA565 | 25 | 100 | 15 | 85 | 9.6
Carlyle | 06EA565 | 25 | 100 | 20 | 80 | 10.3
Carlyle | 06EA565 | 25 | 100 | 25 | 75 | 11.1
Carlyle | 06EA565 | 25 | 100 | 30 | 70 | 12
Carlyle | 06EA565 | 25 | 100 | 35 | 65 | 13
Carlyle | 06EA565 | 25 | 90 | 10 | 80 | 10.4
Carlyle | 06EA565 | 25 | 90 | 15 | 75 | 11.2
Carlyle | 06EA565 | 25 | 90 | 20 | 70 | 12.1
Carlyle | 06EA565 | 25 | 90 | 25 | 65 | 13.1
Carlyle | 06EA565 | 25 | 90 | 30 | 60 | 14.2
Carlyle | 06EA565 | 25 | 90 | 35 | 55 | 15.5
Carlyle | 06EA565 | 25 | 80 | 10 | 70 | 12.2
Carlyle | 06EA565 | 25 | 80 | 15 | 65 | 13.2
Carlyle | 06EA565 | 25 | 80 | 20 | 60 | 14.4
Carlyle | 06EA565 | 25 | 80 | 25 | 55 | 15.6
Carlyle | 06EA565 | 25 | 80 | 30 | 50 | 17.1
Carlyle | 06EA565 | 25 | 80 | 35 | 45 | 18.7
Carlyle | 06EA565 | 25 | 70 | 10 | 60 | 14.5
Carlyle | 06EA565 | 25 | 70 | 15 | 55 | 15.8
Carlyle | 06EA565 | 25 | 70 | 20 | 50 | 17.3
Carlyle | 06EA565 | 25 | 70 | 25 | 45 | 18.9
Carlyle | 06EA565 | 25 | 70 | 30 | 40 | 20.8
Carlyle | 06EA565 | 25 | 70 | 35 | 35 | 22.9
Carlyle | 06DR337 | 10 | 110 | 10 | 100 | 7.9
Carlyle | 06DR337 | 10 | 110 | 15 | 95 | 8.5
Carlyle | 06DR337 | 10 | 110 | 20 | 90 | 9.2
Carlyle | 06DR337 | 10 | 110 | 25 | 85 | 9.9
Carlyle | 06DR337 | 10 | 110 | 30 | 80 | 10.7
Carlyle | 06DR337 | 10 | 110 | 35 | 75 | 11.6
Carlyle | 06DR337 | 10 | 100 | 10 | 90 | 9.2
Carlyle | 06DR337 | 10 | 100 | 15 | 85 | 10
Carlyle | 06DR337 | 10 | 100 | 20 | 80 | 10.8
Carlyle | 06DR337 | 10 | 100 | 25 | 75 | 11.7
Carlyle | 06DR337 | 10 | 100 | 30 | 70 | 12.7
Carlyle | 06DR337 | 10 | 100 | 35 | 65 | 13.9
Carlyle | 06DR337 | 10 | 90 | 10 | 80 | 10.8
Carlyle | 06DR337 | 10 | 90 | 15 | 75 | 11.7
Carlyle | 06DR337 | 10 | 90 | 20 | 70 | 12.8
Carlyle | 06DR337 | 10 | 90 | 25 | 65 | 13.9
Carlyle | 06DR337 | 10 | 90 | 30 | 60 | 15.2
Carlyle | 06DR337 | 10 | 90 | 35 | 55 | 16.7
Carlyle | 06DR337 | 10 | 80 | 10 | 70 | 12.6
Carlyle | 06DR337 | 10 | 80 | 15 | 65 | 13.8
Carlyle | 06DR337 | 10 | 80 | 20 | 60 | 15.2
Carlyle | 06DR337 | 10 | 80 | 25 | 55 | 16.7
Carlyle | 06DR337 | 10 | 80 | 30 | 50 | 18.3
Carlyle | 06DR337 | 10 | 80 | 35 | 45 | 20.2
Carlyle | 06DR337 | 10 | 70 | 10 | 60 | 14.9
Carlyle | 06DR337 | 10 | 70 | 15 | 55 | 16.4
Carlyle | 06DR337 | 10 | 70 | 20 | 50 | 18.1
Carlyle | 06DR337 | 10 | 70 | 25 | 45 | 20.1
Carlyle | 06DR337 | 10 | 70 | 30 | 40 | 22.2
Carlyle | 06DR337 | 10 | 70 | 35 | 35 | 24.7
Carlyle | 06DR337 | 10 | 110 | -30 | 140 | 4.7
Carlyle | 06DR337 | 10 | 110 | -25 | 135 | 5
Carlyle | 06DR337 | 10 | 110 | -20 | 130 | 5.2
Carlyle | 06DR337 | 10 | 110 | -15 | 125 | 5.6
Carlyle | 06DR337 | 10 | 110 | -10 | 120 | 5.9
Carlyle | 06DR337 | 10 | 110 | -5 | 115 | 6.2
Carlyle | 06DR337 | 10 | 100 | -30 | 130 | 5.4
Carlyle | 06DR337 | 10 | 100 | -25 | 125 | 5.7
Carlyle | 06DR337 | 10 | 100 | -20 | 120 | 6
Carlyle | 06DR337 | 10 | 100 | -15 | 115 | 6.4
Carlyle | 06DR337 | 10 | 100 | -10 | 110 | 6.8
Carlyle | 06DR337 | 10 | 100 | -5 | 105 | 7.2
Carlyle | 06DR337 | 10 | 90 | -30 | 120 | 6.1
Carlyle | 06DR337 | 10 | 90 | -25 | 115 | 6.5
Carlyle | 06DR337 | 10 | 90 | -20 | 110 | 6.9
Carlyle | 06DR337 | 10 | 90 | -15 | 105 | 7.4
Carlyle | 06DR337 | 10 | 90 | -10 | 100 | 7.9
Carlyle | 06DR337 | 10 | 90 | -5 | 95 | 8.4
Carlyle | 06DR337 | 10 | 80 | -30 | 110 | 6.9
Carlyle | 06DR337 | 10 | 80 | -25 | 105 | 7.4
Carlyle | 06DR337 | 10 | 80 | -20 | 100 | 7.9
Carlyle | 06DR337 | 10 | 80 | -15 | 95 | 8.5
Carlyle | 06DR337 | 10 | 80 | -10 | 90 | 9.1
Carlyle | 06DR337 | 10 | 80 | -5 | 85 | 9.7
Carlyle | 06DR337 | 10 | 70 | -30 | 100 | 7.9
Carlyle | 06DR337 | 10 | 70 | -25 | 95 | 8.5
Carlyle | 06DR337 | 10 | 70 | -20 | 90 | 9.1
Carlyle | 06DR337 | 10 | 70 | -15 | 85 | 9.7
Carlyle | 06DR337 | 10 | 70 | -10 | 80 | 10.5
Carlyle | 06DR337 | 10 | 70 | -5 | 75 | 11.3
Carlyle | 06DR316 | 5 | 110 | 10 | 100 | 8
Carlyle | 06DR316 | 5 | 110 | 15 | 95 | 8.6
Carlyle | 06DR316 | 5 | 110 | 20 | 90 | 9.3
Carlyle | 06DR316 | 5 | 110 | 25 | 85 | 10
Carlyle | 06DR316 | 5 | 110 | 30 | 80 | 10.8
Carlyle | 06DR316 | 5 | 110 | 35 | 75 | 11.6
Carlyle | 06DR316 | 5 | 100 | 10 | 90 | 9.4
Carlyle | 06DR316 | 5 | 100 | 15 | 85 | 10.1
Carlyle | 06DR316 | 5 | 100 | 20 | 80 | 10.9
Carlyle | 06DR316 | 5 | 100 | 25 | 75 | 11.8
Carlyle | 06DR316 | 5 | 100 | 30 | 70 | 12.7
Carlyle | 06DR316 | 5 | 100 | 35 | 65 | 13.7
Carlyle | 06DR316 | 5 | 90 | 10 | 80 | 10.9
Carlyle | 06DR316 | 5 | 90 | 15 | 75 | 11.8
Carlyle | 06DR316 | 5 | 90 | 20 | 70 | 12.8
Carlyle | 06DR316 | 5 | 90 | 25 | 65 | 13.9
Carlyle | 06DR316 | 5 | 90 | 30 | 60 | 15
Carlyle | 06DR316 | 5 | 90 | 35 | 55 | 16.2
Carlyle | 06DR316 | 5 | 80 | 10 | 70 | 12.8
Carlyle | 06DR316 | 5 | 80 | 15 | 65 | 13.9
Carlyle | 06DR316 | 5 | 80 | 20 | 60 | 15
Carlyle | 06DR316 | 5 | 80 | 25 | 55 | 16.3
Carlyle | 06DR316 | 5 | 80 | 30 | 50 | 17.8
Carlyle | 06DR316 | 5 | 80 | 35 | 45 | 19.3
Carlyle | 06DR316 | 5 | 70 | 10 | 60 | 14.9
Carlyle | 06DR316 | 5 | 70 | 15 | 55 | 16.3
Carlyle | 06DR316 | 5 | 70 | 20 | 50 | 17.7
Carlyle | 06DR316 | 5 | 70 | 25 | 45 | 19.3
Carlyle | 06DR316 | 5 | 70 | 30 | 40 | 21.1
Carlyle | 06DR316 | 5 | 70 | 35 | 35 | 23.1
Carlyle | 06DR316 | 5 | 110 | -30 | 140 | 4.3
Carlyle | 06DR316 | 5 | 110 | -25 | 135 | 4.7
Carlyle | 06DR316 | 5 | 110 | -20 | 130 | 5
Carlyle | 06DR316 | 5 | 110 | -15 | 125 | 5.5
Carlyle | 06DR316 | 5 | 110 | -10 | 120 | 5.9
Carlyle | 06DR316 | 5 | 110 | -5 | 115 | 6.4
Carlyle | 06DR316 | 5 | 100 | -30 | 130 | 4.9
Carlyle | 06DR316 | 5 | 100 | -25 | 125 | 5.4
Carlyle | 06DR316 | 5 | 100 | -20 | 120 | 5.8
Carlyle | 06DR316 | 5 | 100 | -15 | 115 | 6.3
Carlyle | 06DR316 | 5 | 100 | -10 | 110 | 6.9
Carlyle | 06DR316 | 5 | 100 | -5 | 105 | 7.4
Carlyle | 06DR316 | 5 | 90 | -30 | 120 | 5.7
Carlyle | 06DR316 | 5 | 90 | -25 | 115 | 6.2
Carlyle | 06DR316 | 5 | 90 | -20 | 110 | 6.7
Carlyle | 06DR316 | 5 | 90 | -15 | 105 | 7.3
Carlyle | 06DR316 | 5 | 90 | -10 | 100 | 7.9
Carlyle | 06DR316 | 5 | 90 | -5 | 95 | 8.6
Carlyle | 06DR316 | 5 | 80 | -30 | 110 | 6.5
Carlyle | 06DR316 | 5 | 80 | -25 | 105 | 7.1
Carlyle | 06DR316 | 5 | 80 | -20 | 100 | 7.7
Carlyle | 06DR316 | 5 | 80 | -15 | 95 | 8.4
Carlyle | 06DR316 | 5 | 80 | -10 | 90 | 9.2
Carlyle | 06DR316 | 5 | 80 | -5 | 85 | 10
Carlyle | 06DR316 | 5 | 70 | -30 | 100 | 7.4
Carlyle | 06DR316 | 5 | 70 | -25 | 95 | 8.2
Carlyle | 06DR316 | 5 | 70 | -20 | 90 | 8.9
Carlyle | 06DR316 | 5 | 70 | -15 | 85 | 9.7
Carlyle | 06DR316 | 5 | 70 | -10 | 80 | 10.6
Carlyle | 06DR316 | 5 | 70 | -5 | 75 | 11.6
Carlyle | 06EM475 | 25 | 110 | 10 | 100 | 7.8
Carlyle | 06EM475 | 25 | 110 | 15 | 95 | 8.3
Carlyle | 06EM475 | 25 | 110 | 20 | 90 | 8.9
Carlyle | 06EM475 | 25 | 110 | 25 | 85 | 9.5
Carlyle | 06EM475 | 25 | 110 | 30 | 80 | 10.2
Carlyle | 06EM475 | 25 | 110 | 35 | 75 | 10.9
Carlyle | 06EM475 | 25 | 100 | 10 | 90 | 9
Carlyle | 06EM475 | 25 | 100 | 15 | 85 | 9.7
Carlyle | 06EM475 | 25 | 100 | 20 | 80 | 10.4
Carlyle | 06EM475 | 25 | 100 | 25 | 75 | 11.1
Carlyle | 06EM475 | 25 | 100 | 30 | 70 | 12
Carlyle | 06EM475 | 25 | 100 | 35 | 65 | 12.9
Carlyle | 06EM475 | 25 | 90 | 10 | 80 | 10.5
Carlyle | 06EM475 | 25 | 90 | 15 | 75 | 11.3
Carlyle | 06EM475 | 25 | 90 | 20 | 70 | 12.2
Carlyle | 06EM475 | 25 | 90 | 25 | 65 | 13.1
Carlyle | 06EM475 | 25 | 90 | 30 | 60 | 14.2
Carlyle | 06EM475 | 25 | 90 | 35 | 55 | 15.4
Carlyle | 06EM475 | 25 | 80 | 10 | 70 | 12.3
Carlyle | 06EM475 | 25 | 80 | 15 | 65 | 13.3
Carlyle | 06EM475 | 25 | 80 | 20 | 60 | 14.5
Carlyle | 06EM475 | 25 | 80 | 25 | 55 | 15.7
Carlyle | 06EM475 | 25 | 80 | 30 | 50 | 17.1
Carlyle | 06EM475 | 25 | 80 | 35 | 45 | 18.7
Carlyle | 06EM475 | 25 | 70 | 10 | 60 | 14.7
Carlyle | 06EM475 | 25 | 70 | 15 | 55 | 16
Carlyle | 06EM475 | 25 | 70 | 20 | 50 | 17.5
Carlyle | 06EM475 | 25 | 70 | 25 | 45 | 19.1
Carlyle | 06EM475 | 25 | 70 | 30 | 40 | 21
Carlyle | 06EM475 | 25 | 70 | 35 | 35 | 23.3
Carlyle | 06ER450 | 15 | 110 | -30 | 140 | 4.3
Carlyle | 06ER450 | 15 | 110 | -25 | 135 | 4.6
Carlyle | 06ER450 | 15 | 110 | -20 | 130 | 5
Carlyle | 06ER450 | 15 | 110 | -15 | 125 | 5.3
Carlyle | 06ER450 | 15 | 110 | -10 | 120 | 5.6
Carlyle | 06ER450 | 15 | 110 | -5 | 115 | 6
Carlyle | 06ER450 | 15 | 100 | -30 | 130 | 4.8
Carlyle | 06ER450 | 15 | 100 | -25 | 125 | 5.2
Carlyle | 06ER450 | 15 | 100 | -20 | 120 | 5.6
Carlyle | 06ER450 | 15 | 100 | -15 | 115 | 6
Carlyle | 06ER450 | 15 | 100 | -10 | 110 | 6.4
Carlyle | 06ER450 | 15 | 100 | -5 | 105 | 6.8
Carlyle | 06ER450 | 15 | 90 | -30 | 120 | 5.5
Carlyle | 06ER450 | 15 | 90 | -25 | 115 | 5.9
Carlyle | 06ER450 | 15 | 90 | -20 | 110 | 6.3
Carlyle | 06ER450 | 15 | 90 | -15 | 105 | 6.7
Carlyle | 06ER450 | 15 | 90 | -10 | 100 | 7.2
Carlyle | 06ER450 | 15 | 90 | -5 | 95 | 7.7
Carlyle | 06ER450 | 15 | 80 | -30 | 110 | 6.2
Carlyle | 06ER450 | 15 | 80 | -25 | 105 | 6.7
Carlyle | 06ER450 | 15 | 80 | -20 | 100 | 7.2
Carlyle | 06ER450 | 15 | 80 | -15 | 95 | 7.7
Carlyle | 06ER450 | 15 | 80 | -10 | 90 | 8.3
Carlyle | 06ER450 | 15 | 80 | -5 | 85 | 8.8
Carlyle | 06ER450 | 15 | 70 | -30 | 100 | 7.3
Carlyle | 06ER450 | 15 | 70 | -25 | 95 | 7.8
Carlyle | 06ER450 | 15 | 70 | -20 | 90 | 8.4
Carlyle | 06ER450 | 15 | 70 | -15 | 85 | 9
Carlyle | 06ER450 | 15 | 70 | -10 | 80 | 9.7
Carlyle | 06ER450 | 15 | 70 | -5 | 75 | 10.4
Carlyle | 06DR718 | 5 | 110 | -30 | 140 | 4.5
Carlyle | 06DR718 | 5 | 110 | -25 | 135 | 4.9
Carlyle | 06DR718 | 5 | 110 | -20 | 130 | 5.2
Carlyle | 06DR718 | 5 | 110 | -15 | 125 | 5.6
Carlyle | 06DR718 | 5 | 110 | -10 | 120 | 6
Carlyle | 06DR718 | 5 | 110 | -5 | 115 | 6.4
Carlyle | 06DR718 | 5 | 100 | -30 | 130 | 5.1
Carlyle | 06DR718 | 5 | 100 | -25 | 125 | 5.5
Carlyle | 06DR718 | 5 | 100 | -20 | 120 | 5.9
Carlyle | 06DR718 | 5 | 100 | -15 | 115 | 6.4
Carlyle | 06DR718 | 5 | 100 | -10 | 110 | 6.8
Carlyle | 06DR718 | 5 | 100 | -5 | 105 | 7.3
Carlyle | 06DR718 | 5 | 90 | -30 | 120 | 5.8
Carlyle | 06DR718 | 5 | 90 | -25 | 115 | 6.3
Carlyle | 06DR718 | 5 | 90 | -20 | 110 | 6.7
Carlyle | 06DR718 | 5 | 90 | -15 | 105 | 7.3
Carlyle | 06DR718 | 5 | 90 | -10 | 100 | 7.8
Carlyle | 06DR718 | 5 | 90 | -5 | 95 | 8.4
Carlyle | 06DR718 | 5 | 80 | -30 | 110 | 6.6
Carlyle | 06DR718 | 5 | 80 | -25 | 105 | 7.1
Carlyle | 06DR718 | 5 | 80 | -20 | 100 | 7.7
Carlyle | 06DR718 | 5 | 80 | -15 | 95 | 8.3
Carlyle | 06DR718 | 5 | 80 | -10 | 90 | 8.9
Carlyle | 06DR718 | 5 | 80 | -5 | 85 | 9.6
Carlyle | 06DR718 | 5 | 70 | -30 | 100 | 7.4
Carlyle | 06DR718 | 5 | 70 | -25 | 95 | 8
Carlyle | 06DR718 | 5 | 70 | -20 | 90 | 8.7
Carlyle | 06DR718 | 5 | 70 | -15 | 85 | 9.4
Carlyle | 06DR718 | 5 | 70 | -10 | 80 | 10.2
Carlyle | 06DR718 | 5 | 70 | -5 | 75 | 11
Carlyle | 06DM337 | 10 | 110 | 10 | 100 | 7.5
Carlyle | 06DM337 | 10 | 110 | 15 | 95 | 8
Carlyle | 06DM337 | 10 | 110 | 20 | 90 | 8.7
Carlyle | 06DM337 | 10 | 110 | 25 | 85 | 9.3
Carlyle | 06DM337 | 10 | 110 | 30 | 80 | 10.1
Carlyle | 06DM337 | 10 | 110 | 35 | 75 | 10.9
Carlyle | 06DM337 | 10 | 100 | 10 | 90 | 8.8
Carlyle | 06DM337 | 10 | 100 | 15 | 85 | 9.5
Carlyle | 06DM337 | 10 | 100 | 20 | 80 | 10.3
Carlyle | 06DM337 | 10 | 100 | 25 | 75 | 11.2
Carlyle | 06DM337 | 10 | 100 | 30 | 70 | 12.2
Carlyle | 06DM337 | 10 | 100 | 35 | 65 | 13.2
Carlyle | 06DM337 | 10 | 90 | 10 | 80 | 10.5
Carlyle | 06DM337 | 10 | 90 | 15 | 75 | 11.4
Carlyle | 06DM337 | 10 | 90 | 20 | 70 | 12.4
Carlyle | 06DM337 | 10 | 90 | 25 | 65 | 13.5
Carlyle | 06DM337 | 10 | 90 | 30 | 60 | 14.7
Carlyle | 06DM337 | 10 | 90 | 35 | 55 | 16.1
Carlyle | 06DM337 | 10 | 80 | 10 | 70 | 12.4
Carlyle | 06DM337 | 10 | 80 | 15 | 65 | 13.6
Carlyle | 06DM337 | 10 | 80 | 20 | 60 | 14.9
Carlyle | 06DM337 | 10 | 80 | 25 | 55 | 16.3
Carlyle | 06DM337 | 10 | 80 | 30 | 50 | 17.9
Carlyle | 06DM337 | 10 | 80 | 35 | 45 | 19.7
Carlyle | 06DM337 | 10 | 70 | 10 | 60 | 14.7
Carlyle | 06DM337 | 10 | 70 | 15 | 55 | 16.2
Carlyle | 06DM337 | 10 | 70 | 20 | 50 | 17.9
Carlyle | 06DM337 | 10 | 70 | 25 | 45 | 19.7
Carlyle | 06DM337 | 10 | 70 | 30 | 40 | 21.8
Carlyle | 06DM337 | 10 | 70 | 35 | 35 | 24.1
Carlyle | 06DR724 | 6.5 | 110 | 10 | 100 | 7.9
Carlyle | 06DR724 | 6.5 | 110 | 15 | 95 | 8.5
Carlyle | 06DR724 | 6.5 | 110 | 20 | 90 | 9.2
Carlyle | 06DR724 | 6.5 | 110 | 25 | 85 | 9.9
Carlyle | 06DR724 | 6.5 | 110 | 30 | 80 | 10.8
Carlyle | 06DR724 | 6.5 | 110 | 35 | 75 | 11.7
Carlyle | 06DR724 | 6.5 | 100 | 10 | 90 | 9.3
Carlyle | 06DR724 | 6.5 | 100 | 15 | 85 | 10
Carlyle | 06DR724 | 6.5 | 100 | 20 | 80 | 10.9
Carlyle | 06DR724 | 6.5 | 100 | 25 | 75 | 11.9
Carlyle | 06DR724 | 6.5 | 100 | 30 | 70 | 12.9
Carlyle | 06DR724 | 6.5 | 100 | 35 | 65 | 14.2
Carlyle | 06DR724 | 6.5 | 90 | 10 | 80 | 10.9
Carlyle | 06DR724 | 6.5 | 90 | 15 | 75 | 11.8
Carlyle | 06DR724 | 6.5 | 90 | 20 | 70 | 12.9
Carlyle | 06DR724 | 6.5 | 90 | 25 | 65 | 14.2
Carlyle | 06DR724 | 6.5 | 90 | 30 | 60 | 15.5
Carlyle | 06DR724 | 6.5 | 90 | 35 | 55 | 17.1
Carlyle | 06DR724 | 6.5 | 80 | 10 | 70 | 12.8
Carlyle | 06DR724 | 6.5 | 80 | 15 | 65 | 14
Carlyle | 06DR724 | 6.5 | 80 | 20 | 60 | 15.4
Carlyle | 06DR724 | 6.5 | 80 | 25 | 55 | 17
Carlyle | 06DR724 | 6.5 | 80 | 30 | 50 | 18.7
Carlyle | 06DR724 | 6.5 | 80 | 35 | 45 | 20.7
Carlyle | 06DR724 | 6.5 | 70 | 10 | 60 | 15.1
Carlyle | 06DR724 | 6.5 | 70 | 15 | 55 | 16.7
Carlyle | 06DR724 | 6.5 | 70 | 20 | 50 | 18.4
Carlyle | 06DR724 | 6.5 | 70 | 25 | 45 | 20.4
Carlyle | 06DR724 | 6.5 | 70 | 30 | 40 | 22.6
Carlyle | 06DR724 | 6.5 | 70 | 35 | 35 | 25.1
Carlyle | 06DR228 | 7.5 | 110 | 10 | 100 | 7.9
Carlyle | 06DR228 | 7.5 | 110 | 15 | 95 | 8.5
Carlyle | 06DR228 | 7.5 | 110 | 20 | 90 | 9.2
Carlyle | 06DR228 | 7.5 | 110 | 25 | 85 | 9.9
Carlyle | 06DR228 | 7.5 | 110 | 30 | 80 | 10.7
Carlyle | 06DR228 | 7.5 | 110 | 35 | 75 | 11.6
Carlyle | 06DR228 | 7.5 | 100 | 10 | 90 | 9.2
Carlyle | 06DR228 | 7.5 | 100 | 15 | 85 | 10
Carlyle | 06DR228 | 7.5 | 100 | 20 | 80 | 10.8
Carlyle | 06DR228 | 7.5 | 100 | 25 | 75 | 11.7
Carlyle | 06DR228 | 7.5 | 100 | 30 | 70 | 12.8
Carlyle | 06DR228 | 7.5 | 100 | 35 | 65 | 13.9
Carlyle | 06DR228 | 7.5 | 90 | 10 | 80 | 10.8
Carlyle | 06DR228 | 7.5 | 90 | 15 | 75 | 11.7
Carlyle | 06DR228 | 7.5 | 90 | 20 | 70 | 12.8
Carlyle | 06DR228 | 7.5 | 90 | 25 | 65 | 13.9
Carlyle | 06DR228 | 7.5 | 90 | 30 | 60 | 15.3
Carlyle | 06DR228 | 7.5 | 90 | 35 | 55 | 16.7
Carlyle | 06DR228 | 7.5 | 80 | 10 | 70 | 12.6
Carlyle | 06DR228 | 7.5 | 80 | 15 | 65 | 13.8
Carlyle | 06DR228 | 7.5 | 80 | 20 | 60 | 15.2
Carlyle | 06DR228 | 7.5 | 80 | 25 | 55 | 16.7
Carlyle | 06DR228 | 7.5 | 80 | 30 | 50 | 18.3
Carlyle | 06DR228 | 7.5 | 80 | 35 | 45 | 20.2
Carlyle | 06DR228 | 7.5 | 70 | 10 | 60 | 14.9
Carlyle | 06DR228 | 7.5 | 70 | 15 | 55 | 16.4
Carlyle | 06DR228 | 7.5 | 70 | 20 | 50 | 18.1
Carlyle | 06DR228 | 7.5 | 70 | 25 | 45 | 20
Carlyle | 06DR228 | 7.5 | 70 | 30 | 40 | 22.2
Carlyle | 06DR228 | 7.5 | 70 | 35 | 35 | 24.7
Carlyle | 06DM316 | 5 | 110 | 10 | 100 | 7.5
Carlyle | 06DM316 | 5 | 110 | 15 | 95 | 8.2
Carlyle | 06DM316 | 5 | 110 | 20 | 90 | 9
Carlyle | 06DM316 | 5 | 110 | 25 | 85 | 9.9
Carlyle | 06DM316 | 5 | 110 | 30 | 80 | 10.9
Carlyle | 06DM316 | 5 | 110 | 35 | 75 | 12
Carlyle | 06DM316 | 5 | 100 | 10 | 90 | 8.9
Carlyle | 06DM316 | 5 | 100 | 15 | 85 | 9.8
Carlyle | 06DM316 | 5 | 100 | 20 | 80 | 10.7
Carlyle | 06DM316 | 5 | 100 | 25 | 75 | 11.8
Carlyle | 06DM316 | 5 | 100 | 30 | 70 | 13.1
Carlyle | 06DM316 | 5 | 100 | 35 | 65 | 14.5
Carlyle | 06DM316 | 5 | 90 | 10 | 80 | 10.5
Carlyle | 06DM316 | 5 | 90 | 15 | 75 | 11.6
Carlyle | 06DM316 | 5 | 90 | 20 | 70 | 12.8
Carlyle | 06DM316 | 5 | 90 | 25 | 65 | 14.2
Carlyle | 06DM316 | 5 | 90 | 30 | 60 | 15.8
Carlyle | 06DM316 | 5 | 90 | 35 | 55 | 17.6
Carlyle | 06DM316 | 5 | 80 | 10 | 70 | 12.4
Carlyle | 06DM316 | 5 | 80 | 15 | 65 | 13.9
Carlyle | 06DM316 | 5 | 80 | 20 | 60 | 15.4
Carlyle | 06DM316 | 5 | 80 | 25 | 55 | 17.2
Carlyle | 06DM316 | 5 | 80 | 30 | 50 | 19.2
Carlyle | 06DM316 | 5 | 80 | 35 | 45 | 21.5
Carlyle | 06DM316 | 5 | 70 | 10 | 60 | 14.9
Carlyle | 06DM316 | 5 | 70 | 15 | 55 | 16.6
Carlyle | 06DM316 | 5 | 70 | 20 | 50 | 18.7
Carlyle | 06DM316 | 5 | 70 | 25 | 45 | 20.9
Carlyle | 06DM316 | 5 | 70 | 30 | 40 | 23.5
Carlyle | 06DM316 | 5 | 70 | 35 | 35 | 26.5
IR | IR4C0770S | 4 | 70 | -30 | 100 | 7.71
IR | IR4C0770S | 4 | 70 | -25 | 95 | 8.3439
IR | IR4C0770S | 4 | 70 | -20 | 90 | 9.0297
IR | IR4C0770S | 4 | 70 | -15 | 85 | 9.7742
IR | IR4C0770S | 4 | 70 | -10 | 80 | 10.5901
IR | IR4C0770S | 4 | 70 | -5 | 75 | 11.4886
IR | IR4C0770S | 4 | 70 | 0 | 70 | 12.4866
IR | IR4C0770S | 4 | 70 | 5 | 65 | 13.6049
IR | IR4C0770S | 4 | 70 | 10 | 60 | 14.8683
IR | IR4C0770S | 4 | 70 | 15 | 55 | 16.3053
IR | IR4C0770S | 4 | 70 | 20 | 50 | 17.9547
IR | IR4C0770S | 4 | 70 | 30 | 40 | 22.1037
IR | IR4C0770S | 4 | 80 | -30 | 110 | 6.8051
IR | IR4C0770S | 4 | 80 | -25 | 105 | 7.3401
IR | IR4C0770S | 4 | 80 | -20 | 100 | 7.9144
IR | IR4C0770S | 4 | 80 | -15 | 95 | 8.5335
IR | IR4C0770S | 4 | 80 | -10 | 90 | 9.2022
IR | IR4C0770S | 4 | 80 | -5 | 85 | 9.9321
IR | IR4C0770S | 4 | 80 | 0 | 80 | 10.7324
IR | IR4C0770S | 4 | 80 | 5 | 75 | 11.6155
IR | IR4C0770S | 4 | 80 | 10 | 70 | 12.5978
IR | IR4C0770S | 4 | 80 | 15 | 65 | 13.6937
IR | IR4C0770S | 4 | 80 | 20 | 60 | 14.9257
IR | IR4C0770S | 4 | 80 | 30 | 50 | 17.9086
IR | IR4C0770S | 4 | 90 | -30 | 120 | 6.0427
IR | IR4C0770S | 4 | 90 | -25 | 115 | 6.4897
IR | IR4C0770S | 4 | 90 | -20 | 110 | 6.97
IR | IR4C0770S | 4 | 90 | -15 | 105 | 7.4862
IR | IR4C0770S | 4 | 90 | -10 | 100 | 8.0409
IR | IR4C0770S | 4 | 90 | -5 | 95 | 8.6402
IR | IR4C0770S | 4 | 90 | 0 | 90 | 9.2937
IR | IR4C0770S | 4 | 90 | 5 | 85 | 10.0067
IR | IR4C0770S | 4 | 90 | 10 | 80 | 10.7877
IR | IR4C0770S | 4 | 90 | 15 | 75 | 11.6497
IR | IR4C0770S | 4 | 90 | 20 | 70 | 12.6008
IR | IR4C0770S | 4 | 90 | 30 | 60 | 14.8423
IR | IR4C0770S | 4 | 100 | -30 | 130 | 5.3339
IR | IR4C0770S | 4 | 100 | -25 | 125 | 5.7085
IR | IR4C0770S | 4 | 100 | -20 | 120 | 6.1126
IR | IR4C0770S | 4 | 100 | -15 | 115 | 6.546
IR | IR4C0770S | 4 | 100 | -10 | 110 | 7.0109
IR | IR4C0770S | 4 | 100 | -5 | 105 | 7.5106
IR | IR4C0770S | 4 | 100 | 0 | 100 | 8.0504
IR | IR4C0770S | 4 | 100 | 5 | 95 | 8.6361
IR | IR4C0770S | 4 | 100 | 10 | 90 | 9.2696
IR | IR4C0770S | 4 | 100 | 15 | 85 | 9.9614
IR | IR4C0770S | 4 | 100 | 20 | 80 | 10.7147
IR | IR4C0770S | 4 | 100 | 30 | 70 | 12.4445
IR | IR4C0770S | 4 | 110 | -30 | 140 | 4.6339
IR | IR4C0770S | 4 | 110 | -25 | 135 | 4.9538
IR | IR4C0770S | 4 | 110 | -20 | 130 | 5.2981
IR | IR4C0770S | 4 | 110 | -15 | 125 | 5.6674
IR | IR4C0770S | 4 | 110 | -10 | 120 | 6.062
IR | IR4C0770S | 4 | 110 | -5 | 115 | 6.4837
IR | IR4C0770S | 4 | 110 | 0 | 110 | 6.936
IR | IR4C0770S | 4 | 110 | 5 | 105 | 7.4212
IR | IR4C0770S | 4 | 110 | 10 | 100 | 7.9432
IR | IR4C0770S | 4 | 110 | 15 | 95 | 8.5044
IR | IR4C0770S | 4 | 110 | 20 | 90 | 9.1102
IR | IR4C0770S | 4 | 110 | 30 | 80 | 10.4693
IR | IR4C0969S | 5 | 70 | -30 | 100 | 7.4887
IR | IR4C0969S | 5 | 70 | -25 | 95 | 8.1093
IR | IR4C0969S | 5 | 70 | -20 | 90 | 8.8002
IR | IR4C0969S | 5 | 70 | -15 | 85 | 9.567
IR | IR4C0969S | 5 | 70 | -10 | 80 | 10.4162
IR | IR4C0969S | 5 | 70 | -5 | 75 | 11.3552
IR | IR4C0969S | 5 | 70 | 0 | 70 | 12.4044
IR | IR4C0969S | 5 | 70 | 5 | 65 | 13.5797
IR | IR4C0969S | 5 | 70 | 10 | 60 | 14.9065
IR | IR4C0969S | 5 | 70 | 15 | 55 | 16.4128
IR | IR4C0969S | 5 | 70 | 20 | 50 | 18.1382
IR | IR4C0969S | 5 | 70 | 30 | 40 | 22.4453
IR | IR4C0969S | 5 | 80 | -30 | 110 | 6.5672
IR | IR4C0969S | 5 | 80 | -25 | 105 | 7.0798
IR | IR4C0969S | 5 | 80 | -20 | 100 | 7.6455
IR | IR4C0969S | 5 | 80 | -15 | 95 | 8.2662
IR | IR4C0969S | 5 | 80 | -10 | 90 | 8.9434
IR | IR4C0969S | 5 | 80 | -5 | 85 | 9.6897
IR | IR4C0969S | 5 | 80 | 0 | 80 | 10.5112
IR | IR4C0969S | 5 | 80 | 5 | 75 | 11.4213
IR | IR4C0969S | 5 | 80 | 10 | 70 | 12.4374
IR | IR4C0969S | 5 | 80 | 15 | 65 | 13.5766
IR | IR4C0969S | 5 | 80 | 20 | 60 | 14.8573
IR | IR4C0969S | 5 | 80 | 30 | 50 | 17.9728
IR | IR4C0969S | 5 | 90 | -30 | 120 | 5.7615
IR | IR4C0969S | 5 | 90 | -25 | 115 | 6.1892
IR | IR4C0969S | 5 | 90 | -20 | 110 | 6.6611
IR | IR4C0969S | 5 | 90 | -15 | 105 | 7.1713
IR | IR4C0969S | 5 | 90 | -10 | 100 | 7.7232
IR | IR4C0969S | 5 | 90 | -5 | 95 | 8.3233
IR | IR4C0969S | 5 | 90 | 0 | 90 | 8.9803
IR | IR4C0969S | 5 | 90 | 5 | 85 | 9.7005
IR | IR4C0969S | 5 | 90 | 10 | 80 | 10.4971
IR | IR4C0969S | 5 | 90 | 15 | 75 | 11.377
IR | IR4C0969S | 5 | 90 | 20 | 70 | 12.3602
IR | IR4C0969S | 5 | 90 | 30 | 60 | 14.6967
IR | IR4C0969S | 5 | 100 | -30 | 130 | 4.9987
IR | IR4C0969S | 5 | 100 | -25 | 125 | 5.3938
IR | IR4C0969S | 5 | 100 | -20 | 120 | 5.7919
IR | IR4C0969S | 5 | 100 | -15 | 115 | 6.2152
IR | IR4C0969S | 5 | 100 | -10 | 110 | 6.6698
IR | IR4C0969S | 5 | 100 | -5 | 105 | 7.1606
IR | IR4C0969S | 5 | 100 | 0 | 100 | 7.6941
IR | IR4C0969S | 5 | 100 | 5 | 95 | 8.2728
IR | IR4C0969S | 5 | 100 | 10 | 90 | 8.9065
IR | IR4C0969S | 5 | 100 | 15 | 85 | 9.6043
IR | IR4C0969S | 5 | 100 | 20 | 80 | 10.3716
IR | IR4C0969S | 5 | 100 | 30 | 70 | 12.1698
IR | IR4C0969S | 5 | 110 | -30 | 140 | 4.3543
IR | IR4C0969S | 5 | 110 | -25 | 135 | 4.6655
IR | IR4C0969S | 5 | 110 | -20 | 130 | 5.0048
IR | IR4C0969S | 5 | 110 | -15 | 125 | 5.36
IR | IR4C0969S | 5 | 110 | -10 | 120 | 5.7398
IR | IR4C0969S | 5 | 110 | -5 | 115 | 6.1453
IR | IR4C0969S | 5 | 110 | 0 | 110 | 6.5803
IR | IR4C0969S | 5 | 110 | 5 | 105 | 7.0522
IR | IR4C0969S | 5 | 110 | 10 | 100 | 7.5637
IR | IR4C0969S | 5 | 110 | 15 | 95 | 8.1201
IR | IR4C0969S | 5 | 110 | 20 | 90 | 8.7303
IR | IR4C0969S | 5 | 110 | 30 | 80 | 10.1354
IR | IR4C1145S | 6 | 70 | -30 | 100 | 7.41
IR | IR4C1145S | 6 | 70 | -25 | 95 | 8.0226
IR | IR4C1145S | 6 | 70 | -20 | 90 | 8.7503
IR | IR4C1145S | 6 | 70 | -15 | 85 | 9.5362
IR | IR4C1145S | 6 | 70 | -10 | 80 | 10.4047
IR | IR4C1145S | 6 | 70 | -5 | 75 | 11.3685
IR | IR4C1145S | 6 | 70 | 0 | 70 | 12.4424
IR | IR4C1145S | 6 | 70 | 5 | 65 | 13.6467
IR | IR4C1145S | 6 | 70 | 10 | 60 | 15.004
IR | IR4C1145S | 6 | 70 | 15 | 55 | 16.5476
IR | IR4C1145S | 6 | 70 | 20 | 50 | 18.3103
IR | IR4C1145S | 6 | 70 | 30 | 40 | 22.7058
IR | IR4C1145S | 6 | 80 | -30 | 110 | 6.5072
IR | IR4C1145S | 6 | 80 | -25 | 105 | 7.0319
IR | IR4C1145S | 6 | 80 | -20 | 100 | 7.6103
IR | IR4C1145S | 6 | 80 | -15 | 95 | 8.2474
IR | IR4C1145S | 6 | 80 | -10 | 90 | 8.9432
IR | IR4C1145S | 6 | 80 | -5 | 85 | 9.7103
IR | IR4C1145S | 6 | 80 | 0 | 80 | 10.5565
IR | IR4C1145S | 6 | 80 | 5 | 75 | 11.4935
IR | IR4C1145S | 6 | 80 | 10 | 70 | 12.5398
IR | IR4C1145S | 6 | 80 | 15 | 65 | 13.7124
IR | IR4C1145S | 6 | 80 | 20 | 60 | 15.0331
IR | IR4C1145S | 6 | 80 | 30 | 50 | 18.2449
IR | IR4C1145S | 6 | 90 | -30 | 120 | 5.709
IR | IR4C1145S | 6 | 90 | -25 | 115 | 6.1478
IR | IR4C1145S | 6 | 90 | -20 | 110 | 6.6284
IR | IR4C1145S | 6 | 90 | -15 | 105 | 7.1512
IR | IR4C1145S | 6 | 90 | -10 | 100 | 7.7193
IR | IR4C1145S | 6 | 90 | -5 | 95 | 8.3371
IR | IR4C1145S | 6 | 90 | 0 | 90 | 9.0152
IR | IR4C1145S | 6 | 90 | 5 | 85 | 9.7592
IR | IR4C1145S | 6 | 90 | 10 | 80 | 10.5827
IR | IR4C1145S | 6 | 90 | 15 | 75 | 11.4948
IR | IR4C1145S | 6 | 90 | 20 | 70 | 12.513
IR | IR4C1145S | 6 | 90 | 30 | 60 | 14.9383
IR | IR4C1145S | 6 | 100 | -30 | 130 | 4.9905
IR | IR4C1145S | 6 | 100 | -25 | 125 | 5.3568
IR | IR4C1145S | 6 | 100 | -20 | 120 | 5.7597
IR | IR4C1145S | 6 | 100 | -15 | 115 | 6.1943
IR | IR4C1145S | 6 | 100 | -10 | 110 | 6.6606
IR | IR4C1145S | 6 | 100 | -5 | 105 | 7.1654
IR | IR4C1145S | 6 | 100 | 0 | 100 | 7.7153
IR | IR4C1145S | 6 | 100 | 5 | 95 | 8.3147
IR | IR4C1145S | 6 | 100 | 10 | 90 | 8.9714
IR | IR4C1145S | 6 | 100 | 15 | 85 | 9.6945
IR | IR4C1145S | 6 | 100 | 20 | 80 | 10.4943
IR | IR4C1145S | 6 | 100 | 30 | 70 | 12.3679
IR | IR4C1145S | 6 | 110 | -30 | 140 | 4.3218
IR | IR4C1145S | 6 | 110 | -25 | 135 | 4.6308
IR | IR4C1145S | 6 | 110 | -20 | 130 | 4.9727
IR | IR4C1145S | 6 | 110 | -15 | 125 | 5.3353
IR | IR4C1145S | 6 | 110 | -10 | 120 | 5.7218
IR | IR4C1145S | 6 | 110 | -5 | 115 | 6.1377
IR | IR4C1145S | 6 | 110 | 0 | 110 | 6.5879
IR | IR4C1145S | 6 | 110 | 5 | 105 | 7.0754
IR | IR4C1145S | 6 | 110 | 10 | 100 | 7.6057
IR | IR4C1145S | 6 | 110 | 15 | 95 | 8.1855
IR | IR4C1145S | 6 | 110 | 20 | 90 | 8.8208
IR | IR4C1145S | 6 | 110 | 30 | 80 | 10.2913
IR | IR4C1480S | 7 | 70 | -30 | 100 | 7.71
IR | IR4C1480S | 7 | 70 | -25 | 95 | 8.3439
IR | IR4C1480S | 7 | 70 | -20 | 90 | 9.0297
IR | IR4C1480S | 7 | 70 | -15 | 85 | 9.7742
IR | IR4C1480S | 7 | 70 | -10 | 80 | 10.5901
IR | IR4C1480S | 7 | 70 | -5 | 75 | 11.4886
IR | IR4C1480S | 7 | 70 | 0 | 70 | 12.4866
IR | IR4C1480S | 7 | 70 | 5 | 65 | 13.6049
IR | IR4C1480S | 7 | 70 | 10 | 60 | 14.8683
IR | IR4C1480S | 7 | 70 | 15 | 55 | 16.3053
IR | IR4C1480S | 7 | 70 | 20 | 50 | 17.9547
IR | IR4C1480S | 7 | 70 | 30 | 40 | 22.1037
IR | IR4C1480S | 7 | 80 | -30 | 110 | 6.8051
IR | IR4C1480S | 7 | 80 | -25 | 105 | 7.3401
IR | IR4C1480S | 7 | 80 | -20 | 100 | 7.9144
IR | IR4C1480S | 7 | 80 | -15 | 95 | 8.5335
IR | IR4C1480S | 7 | 80 | -10 | 90 | 9.2022
IR | IR4C1480S | 7 | 80 | -5 | 85 | 9.9321
IR | IR4C1480S | 7 | 80 | 0 | 80 | 10.7324
IR | IR4C1480S | 7 | 80 | 5 | 75 | 11.6155
IR | IR4C1480S | 7 | 80 | 10 | 70 | 12.5978
IR | IR4C1480S | 7 | 80 | 15 | 65 | 13.6937
IR | IR4C1480S | 7 | 80 | 20 | 60 | 14.9257
IR | IR4C1480S | 7 | 80 | 30 | 50 | 17.9086
IR | IR4C1480S | 7 | 90 | -30 | 120 | 6.0427
IR | IR4C1480S | 7 | 90 | -25 | 115 | 6.4897
IR | IR4C1480S | 7 | 90 | -20 | 110 | 6.97
IR | IR4C1480S | 7 | 90 | -15 | 105 | 7.4862
IR | IR4C1480S | 7 | 90 | -10 | 100 | 8.0409
IR | IR4C1480S | 7 | 90 | -5 | 95 | 8.6402
IR | IR4C1480S | 7 | 90 | 0 | 90 | 9.2937
IR | IR4C1480S | 7 | 90 | 5 | 85 | 10.0067
IR | IR4C1480S | 7 | 90 | 10 | 80 | 10.7877
IR | IR4C1480S | 7 | 90 | 15 | 75 | 11.6497
IR | IR4C1480S | 7 | 90 | 20 | 70 | 12.6008
IR | IR4C1480S | 7 | 90 | 30 | 60 | 14.8423
IR | IR4C1480S | 7 | 100 | -30 | 130 | 5.3339
IR | IR4C1480S | 7 | 100 | -25 | 125 | 5.7085
IR | IR4C1480S | 7 | 100 | -20 | 120 | 6.1126
IR | IR4C1480S | 7 | 100 | -15 | 115 | 6.546
IR | IR4C1480S | 7 | 100 | -10 | 110 | 7.0109
IR | IR4C1480S | 7 | 100 | -5 | 105 | 7.5106
IR | IR4C1480S | 7 | 100 | 0 | 100 | 8.0504
IR | IR4C1480S | 7 | 100 | 5 | 95 | 8.6361
IR | IR4C1480S | 7 | 100 | 10 | 90 | 9.2696
IR | IR4C1480S | 7 | 100 | 15 | 85 | 9.9614
IR | IR4C1480S | 7 | 100 | 20 | 80 | 10.7147
IR | IR4C1480S | 7 | 100 | 30 | 70 | 12.4445
IR | IR4C1480S | 7 | 110 | -30 | 140 | 4.6339
IR | IR4C1480S | 7 | 110 | -25 | 135 | 4.9538
IR | IR4C1480S | 7 | 110 | -20 | 130 | 5.2981
IR | IR4C1480S | 7 | 110 | -15 | 125 | 5.6674
IR | IR4C1480S | 7 | 110 | -10 | 120 | 6.062
IR | IR4C1480S | 7 | 110 | -5 | 115 | 6.4837
IR | IR4C1480S | 7 | 110 | 0 | 110 | 6.936
IR | IR4C1480S | 7 | 110 | 5 | 105 | 7.4212
IR | IR4C1480S | 7 | 110 | 10 | 100 | 7.9432
IR | IR4C1480S | 7 | 110 | 15 | 95 | 8.5044
IR | IR4C1480S | 7 | 110 | 20 | 90 | 9.1102
IR | IR4C1480S | 7 | 110 | 30 | 80 | 10.4693
IR | IR4C1761S | 9 | 70 | -30 | 100 | 7.648
IR | IR4C1761S | 9 | 70 | -25 | 95 | 8.271
IR | IR4C1761S | 9 | 70 | -20 | 90 | 8.9486
IR | IR4C1761S | 9 | 70 | -15 | 85 | 9.686
IR | IR4C1761S | 9 | 70 | -10 | 80 | 10.4942
IR | IR4C1761S | 9 | 70 | -5 | 75 | 11.387
IR | IR4C1761S | 9 | 70 | 0 | 70 | 12.3831
IR | IR4C1761S | 9 | 70 | 5 | 65 | 13.4983
IR | IR4C1761S | 9 | 70 | 10 | 60 | 14.7593
IR | IR4C1761S | 9 | 70 | 15 | 55 | 16.1974
IR | IR4C1761S | 9 | 70 | 20 | 50 | 17.8481
IR | IR4C1761S | 9 | 70 | 30 | 40 | 22.0082
IR | IR4C1761S | 9 | 80 | -30 | 110 | 6.7347
IR | IR4C1761S | 9 | 80 | -25 | 105 | 7.2612
IR | IR4C1761S | 9 | 80 | -20 | 100 | 7.8271
IR | IR4C1761S | 9 | 80 | -15 | 95 | 8.436
IR | IR4C1761S | 9 | 80 | -10 | 90 | 9.0965
IR | IR4C1761S | 9 | 80 | -5 | 85 | 9.8167
IR | IR4C1761S | 9 | 80 | 0 | 80 | 10.6077
IR | IR4C1761S | 9 | 80 | 5 | 75 | 11.4792
IR | IR4C1761S | 9 | 80 | 10 | 70 | 12.4483
IR | IR4C1761S | 9 | 80 | 15 | 65 | 13.5313
IR | IR4C1761S | 9 | 80 | 20 | 60 | 14.7493
IR | IR4C1761S | 9 | 80 | 30 | 50 | 17.6986
IR | IR4C1761S | 9 | 90 | -30 | 120 | 5.911
IR | IR4C1761S | 9 | 90 | -25 | 115 | 6.3632
IR | IR4C1761S | 9 | 90 | -20 | 110 | 6.8449
IR | IR4C1761S | 9 | 90 | -15 | 105 | 7.3592
IR | IR4C1761S | 9 | 90 | -10 | 100 | 7.9107
IR | IR4C1761S | 9 | 90 | -5 | 95 | 8.5059
IR | IR4C1761S | 9 | 90 | 0 | 90 | 9.1517
IR | IR4C1761S | 9 | 90 | 5 | 85 | 9.855
IR | IR4C1761S | 9 | 90 | 10 | 80 | 10.6245
IR | IR4C1761S | 9 | 90 | 15 | 75 | 11.4717
IR | IR4C1761S | 9 | 90 | 20 | 70 | 12.4063
IR | IR4C1761S | 9 | 90 | 30 | 60 | 14.604
IR | IR4C1761S | 9 | 100 | -30 | 130 | 5.1658
IR | IR4C1761S | 9 | 100 | -25 | 125 | 5.556
IR | IR4C1761S | 9 | 100 | -20 | 120 | 5.9704
IR | IR4C1761S | 9 | 100 | -15 | 115 | 6.4091
IR | IR4C1761S | 9 | 100 | -10 | 110 | 6.8756
IR | IR4C1761S | 9 | 100 | -5 | 105 | 7.3745
IR | IR4C1761S | 9 | 100 | 0 | 100 | 7.9104
IR | IR4C1761S | 9 | 100 | 5 | 95 | 8.4874
IR | IR4C1761S | 9 | 100 | 10 | 90 | 9.1108
IR | IR4C1761S | 9 | 100 | 15 | 85 | 9.7878
IR | IR4C1761S | 9 | 100 | 20 | 80 | 10.5244
IR | IR4C1761S | 9 | 100 | 30 | 70 | 12.2112
IR | IR4C1761S | 9 | 110 | -30 | 140 | 4.488
IR | IR4C1761S | 9 | 110 | -25 | 135 | 4.8246
IR | IR4C1761S | 9 | 110 | -20 | 130 | 5.1803
IR | IR4C1761S | 9 | 110 | -15 | 125 | 5.5548
IR | IR4C1761S | 9 | 110 | -10 | 120 | 5.9499
IR | IR4C1761S | 9 | 110 | -5 | 115 | 6.3698
IR | IR4C1761S | 9 | 110 | 0 | 110 | 6.8161
IR | IR4C1761S | 9 | 110 | 5 | 105 | 7.2927
IR | IR4C1761S | 9 | 110 | 10 | 100 | 7.8028
IR | IR4C1761S | 9 | 110 | 15 | 95 | 8.3502
IR | IR4C1761S | 9 | 110 | 20 | 90 | 8.9381
IR | IR4C1761S | 9 | 110 | 30 | 80 | 10.2569
IR | IR4C2067S | 10 | 70 | -30 | 100 | 7.7986
IR | IR4C2067S | 10 | 70 | -25 | 95 | 8.437
IR | IR4C2067S | 10 | 70 | -20 | 90 | 9.1277
IR | IR4C2067S | 10 | 70 | -15 | 85 | 9.8771
IR | IR4C2067S | 10 | 70 | -10 | 80 | 10.6944
IR | IR4C2067S | 10 | 70 | -5 | 75 | 11.5924
IR | IR4C2067S | 10 | 70 | 0 | 70 | 12.5873
IR | IR4C2067S | 10 | 70 | 5 | 65 | 13.6973
IR | IR4C2067S | 10 | 70 | 10 | 60 | 14.9438
IR | IR4C2067S | 10 | 70 | 15 | 55 | 16.3567
IR | IR4C2067S | 10 | 70 | 20 | 50 | 17.9682
IR | IR4C2067S | 10 | 70 | 30 | 40 | 21.981
IR | IR4C2067S | 10 | 80 | -30 | 110 | 6.8772
IR | IR4C2067S | 10 | 80 | -25 | 105 | 7.4385
IR | IR4C2067S | 10 | 80 | -20 | 100 | 8.0335
IR | IR4C2067S | 10 | 80 | -15 | 95 | 8.6679
IR | IR4C2067S | 10 | 80 | -10 | 90 | 9.3478
IR | IR4C2067S | 10 | 80 | -5 | 85 | 10.0828
IR | IR4C2067S | 10 | 80 | 0 | 80 | 10.884
IR | IR4C2067S | 10 | 80 | 5 | 75 | 11.7647
IR | IR4C2067S | 10 | 80 | 10 | 70 | 12.7366
IR | IR4C2067S | 10 | 80 | 15 | 65 | 13.8188
IR | IR4C2067S | 10 | 80 | 20 | 60 | 15.0289
IR | IR4C2067S | 10 | 80 | 30 | 50 | 17.9428
IR | IR4C2067S | 10 | 90 | -30 | 120 | 6.0515
IR | IR4C2067S | 10 | 90 | -25 | 115 | 6.5374
IR | IR4C2067S | 10 | 90 | -20 | 110 | 7.0501
IR | IR4C2067S | 10 | 90 | -15 | 105 | 7.5922
IR | IR4C2067S | 10 | 90 | -10 | 100 | 8.1697
IR | IR4C2067S | 10 | 90 | -5 | 95 | 8.7889
IR | IR4C2067S | 10 | 90 | 0 | 90 | 9.4556
IR | IR4C2067S | 10 | 90 | 5 | 85 | 10.179
IR | IR4C2067S | 10 | 90 | 10 | 80 | 10.9653
IR | IR4C2067S | 10 | 90 | 15 | 75 | 11.8262
IR | IR4C2067S | 10 | 90 | 20 | 70 | 12.7724
IR | IR4C2067S | 10 | 90 | 30 | 60 | 14.9779
IR | IR4C2067S | 10 | 100 | -30 | 130 | 5.306
IR | IR4C2067S | 10 | 100 | -25 | 125 | 5.7215
IR | IR4C2067S | 10 | 100 | -20 | 120 | 6.1627
IR | IR4C2067S | 10 | 100 | -15 | 115 | 6.6302
IR | IR4C2067S | 10 | 100 | -10 | 110 | 7.1463
IR | IR4C2067S | 10 | 100 | -5 | 105 | 7.6547
IR | IR4C2067S | 10 | 100 | 0 | 100 | 8.2195
IR | IR4C2067S | 10 | 100 | 5 | 95 | 8.8253
IR | IR4C2067S | 10 | 100 | 10 | 90 | 9.4768
IR | IR4C2067S | 10 | 100 | 15 | 85 | 10.1783
IR | IR4C2067S | 10 | 100 | 20 | 80 | 10.9362
IR | IR4C2067S | 10 | 100 | 30 | 70 | 12.6497
IR | IR4C2067S | 10 | 110 | -30 | 140 | 4.6087
IR | IR4C2067S | 10 | 110 | -25 | 135 | 4.9642
IR | IR4C2067S | 10 | 110 | -20 | 130 | 5.3442
IR | IR4C2067S | 10 | 110 | -15 | 125 | 5.7475
IR | IR4C2067S | 10 | 110 | -10 | 120 | 6.1754
IR | IR4C2067S | 10 | 110 | -5 | 115 | 6.6287
IR | IR4C2067S | 10 | 110 | 0 | 110 | 7.1105
IR | IR4C2067S | 10 | 110 | 5 | 105 | 7.6221
IR | IR4C2067S | 10 | 110 | 10 | 100 | 8.1662
IR | IR4C2067S | 10 | 110 | 15 | 95 | 8.7448
IR | IR4C2067S | 10 | 110 | 20 | 90 | 9.3595
IR | IR4C2067S | 10 | 110 | 30 | 80 | 10.7115
IR | IR4C2397S | 12 | 70 | -30 | 100 | 7.7202
IR | IR4C2397S | 12 | 70 | -25 | 95 | 8.3391
IR | IR4C2397S | 12 | 70 | -20 | 90 | 9.0053
IR | IR4C2397S | 12 | 70 | -15 | 85 | 9.7279
IR | IR4C2397S | 12 | 70 | -10 | 80 | 10.5178
IR | IR4C2397S | 12 | 70 | -5 | 75 | 11.3883
IR | IR4C2397S | 12 | 70 | 0 | 70 | 12.3559
IR | IR4C2397S | 12 | 70 | 5 | 65 | 13.4401
IR | IR4C2397S | 12 | 70 | 10 | 60 | 14.6646
IR | IR4C2397S | 12 | 70 | 15 | 55 | 16.0602
IR | IR4C2397S | 12 | 70 | 20 | 50 | 17.6645
IR | IR4C2397S | 12 | 70 | 30 | 40 | 21.7094
IR | IR4C2397S | 12 | 80 | -30 | 110 | 6.8022
IR | IR4C2397S | 12 | 80 | -25 | 105 | 7.3319
IR | IR4C2397S | 12 | 80 | -20 | 100 | 7.8915
IR | IR4C2397S | 12 | 80 | -15 | 95 | 8.4869
IR | IR4C2397S | 12 | 80 | -10 | 90 | 9.128
IR | IR4C2397S | 12 | 80 | -5 | 85 | 9.8223
IR | IR4C2397S | 12 | 80 | 0 | 80 | 10.5819
IR | IR4C2397S | 12 | 80 | 5 | 75 | 11.4195
IR | IR4C2397S | 12 | 80 | 10 | 70 | 12.3487
IR | IR4C2397S | 12 | 80 | 15 | 65 | 13.3879
IR | IR4C2397S | 12 | 80 | 20 | 60 | 14.557
IR | IR4C2397S | 12 | 80 | 30 | 50 | 17.3978
IR | IR4C2397S | 12 | 90 | -30 | 120 | 6.0092
IR | IR4C2397S | 12 | 90 | -25 | 115 | 6.4772
IR | IR4C2397S | 12 | 90 | -20 | 110 | 6.9638
IR | IR4C2397S | 12 | 90 | -15 | 105 | 7.4734
IR | IR4C2397S | 12 | 90 | -10 | 100 | 8.0134
IR | IR4C2397S | 12 | 90 | -5 | 95 | 8.59
IR | IR4C2397S | 12 | 90 | 0 | 90 | 9.2116
IR | IR4C2397S | 12 | 90 | 5 | 85 | 9.8866
IR | IR4C2397S | 12 | 90 | 10 | 80 | 10.6241
IR | IR4C2397S | 12 | 90 | 15 | 75 | 11.4347
IR | IR4C2397S | 12 | 90 | 20 | 70 | 12.3317
IR | IR4C2397S | 12 | 90 | 30 | 60 | 14.4441
IR | IR4C2397S | 12 | 100 | -30 | 130 | 5.2949
IR | IR4C2397S | 12 | 100 | -25 | 125 | 5.7115
IR | IR4C2397S | 12 | 100 | -20 | 120 | 6.1399
IR | IR4C2397S | 12 | 100 | -15 | 115 | 6.5837
IR | IR4C2397S | 12 | 100 | -10 | 110 | 7.0483
IR | IR4C2397S | 12 | 100 | -5 | 105 | 7.5395
IR | IR4C2397S | 12 | 100 | 0 | 100 | 8.061
IR | IR4C2397S | 12 | 100 | 5 | 95 | 8.6205
IR | IR4C2397S | 12 | 100 | 10 | 90 | 9.2222
IR | IR4C2397S | 12 | 100 | 15 | 85 | 9.8743
IR | IR4C2397S | 12 | 100 | 20 | 80 | 10.583
IR | IR4C2397S | 12 | 100 | 30 | 70 | 12.2089
IR | IR4C2397S | 12 | 110 | -30 | 140 | 4.6224
IR | IR4C2397S | 12 | 110 | -25 | 135 | 4.987
IR | IR4C2397S | 12 | 110 | -20 | 130 | 5.3624
IR | IR4C2397S | 12 | 110 | -15 | 125 | 5.7497
IR | IR4C2397S | 12 | 110 | -10 | 120 | 6.1524
IR | IR4C2397S | 12 | 110 | -5 | 115 | 6.5748
IR | IR4C2397S | 12 | 110 | 0 | 110 | 7.0196
IR | IR4C2397S | 12 | 110 | 5 | 105 | 7.4913
IR | IR4C2397S | 12 | 110 | 10 | 100 | 7.9923
IR | IR4C2397S | 12 | 110 | 15 | 95 | 8.5273
IR | IR4C2397S | 12 | 110 | 20 | 90 | 9.1005
IR | IR4C2397S | 12 | 110 | 30 | 80 | 10.3807
IR | IR4B2707P | 14 | 70 | -30 | 100 | 7.4585
IR | IR4B2707P | 14 | 70 | -25 | 95 | 8.1011
IR | IR4B2707P | 14 | 70 | -20 | 90 | 8.7867
IR | IR4B2707P | 14 | 70 | -15 | 85 | 9.5269
IR | IR4B2707P | 14 | 70 | -10 | 80 | 10.3336
IR | IR4B2707P | 14 | 70 | -5 | 75 | 11.2181
IR | IR4B2707P | 14 | 70 | 0 | 70 | 12.1939
IR | IR4B2707P | 14 | 70 | 5 | 65 | 13.2781
IR | IR4B2707P | 14 | 70 | 10 | 60 | 14.4896
IR | IR4B2707P | 14 | 70 | 15 | 55 | 15.8506
IR | IR4B2707P | 14 | 70 | 20 | 50 | 17.391
IR | IR4B2707P | 14 | 70 | 30 | 40 | 21.1676
IR | IR4B2707P | 14 | 80 | -30 | 110 | 6.6184
IR | IR4B2707P | 14 | 80 | -25 | 105 | 7.1666
IR | IR4B2707P | 14 | 80 | -20 | 100 | 7.7438
IR | IR4B2707P | 14 | 80 | -15 | 95 | 8.3598
IR | IR4B2707P | 14 | 80 | -10 | 90 | 9.025
IR | IR4B2707P | 14 | 80 | -5 | 85 | 9.7461
IR | IR4B2707P | 14 | 80 | 0 | 80 | 10.5336
IR | IR4B2707P | 14 | 80 | 5 | 75 | 11.3974
IR | IR4B2707P | 14 | 80 | 10 | 70 | 12.352
IR | IR4B2707P | 14 | 80 | 15 | 65 | 13.4115
IR | IR4B2707P | 14 | 80 | 20 | 60 | 14.5928
IR | IR4B2707P | 14 | 80 | 30 | 50 | 17.4215
IR | IR4B2707P | 14 | 90 | -30 | 120 | 5.8689
IR | IR4B2707P | 14 | 90 | -25 | 115 | 6.3381
IR | IR4B2707P | 14 | 90 | -20 | 110 | 6.8267
IR | IR4B2707P | 14 | 90 | -15 | 105 | 7.3431
IR | IR4B2707P | 14 | 90 | -10 | 100 | 7.8942
IR | IR4B2707P | 14 | 90 | -5 | 95 | 8.4864
IR | IR4B2707P | 14 | 90 | 0 | 90 | 9.1273
IR | IR4B2707P | 14 | 90 | 5 | 85 | 9.8241
IR | IR4B2707P | 14 | 90 | 10 | 80 | 10.5859
IR | IR4B2707P | 14 | 90 | 15 | 75 | 11.4215
IR | IR4B2707P | 14 | 90 | 20 | 70 | 12.3442
IR | IR4B2707P | 14 | 90 | 30 | 60 | 14.5095
IR | IR4B2707P | 14 | 100 | -30 | 130 | 5.1793
IR | IR4B2707P | 14 | 100 | -25 | 125 | 5.5809
IR | IR4B2707P | 14 | 100 | -20 | 120 | 5.995
IR | IR4B2707P | 14 | 100 | -15 | 115 | 6.4282
IR | IR4B2707P | 14 | 100 | -10 | 110 | 6.8873
IR | IR4B2707P | 14 | 100 | -5 | 105 | 7.3761
IR | IR4B2707P | 14 | 100 | 0 | 100 | 7.9009
IR | IR4B2707P | 14 | 100 | 5 | 95 | 8.4657
IR | IR4B2707P | 14 | 100 | 10 | 90 | 9.0783
IR | IR4B2707P | 14 | 100 | 15 | 85 | 9.7444
IR | IR4B2707P | 14 | 100 | 20 | 80 | 10.4726
IR | IR4B2707P | 14 | 100 | 30 | 70 | 12.153
IR | IR4B2707P | 14 | 110 | -30 | 140 | 4.5345
IR | IR4B2707P | 14 | 110 | -25 | 135 | 4.8773
IR | IR4B2707P | 14 | 110 | -20 | 130 | 5.2277
IR | IR4B2707P | 14 | 110 | -15 | 125 | 5.5909
IR | IR4B2707P | 14 | 110 | -10 | 120 | 5.9726
IR | IR4B2707P | 14 | 110 | -5 | 115 | 6.3787
IR | IR4B2707P | 14 | 110 | 0 | 110 | 6.8063
IR | IR4B2707P | 14 | 110 | 5 | 105 | 7.2661
IR | IR4B2707P | 14 | 110 | 10 | 100 | 7.7602
IR | IR4B2707P | 14 | 110 | 15 | 95 | 8.2935
IR | IR4B2707P | 14 | 110 | 20 | 90 | 8.8714
IR | IR4B2707P | 14 | 110 | 30 | 80 | 10.1868
IR | IR4B3139P | 16 | 70 | -30 | 100 | 7.4736
IR | IR4B3139P | 16 | 70 | -25 | 95 | 8.0961
IR | IR4B3139P | 16 | 70 | -20 | 90 | 8.7598
IR | IR4B3139P | 16 | 70 | -15 | 85 | 9.4762
IR | IR4B3139P | 16 | 70 | -10 | 80 | 10.255
IR | IR4B3139P | 16 | 70 | -5 | 75 | 11.1069
IR | IR4B3139P | 16 | 70 | 0 | 70 | 12.0431
IR | IR4B3139P | 16 | 70 | 5 | 65 | 13.0768
IR | IR4B3139P | 16 | 70 | 10 | 60 | 14.2248
IR | IR4B3139P | 16 | 70 | 15 | 55 | 15.5069
IR | IR4B3139P | 16 | 70 | 20 | 50 | 16.9466
IR | IR4B3139P | 16 | 70 | 30 | 40 | 20.4241
IR | IR4B3139P | 16 | 80 | -30 | 110 | 6.6011
IR | IR4B3139P | 16 | 80 | -25 | 105 | 7.1316
IR | IR4B3139P | 16 | 80 | -20 | 100 | 7.6901
IR | IR4B3139P | 16 | 80 | -15 | 95 | 8.2848
IR | IR4B3139P | 16 | 80 | -10 | 90 | 8.9252
IR | IR4B3139P | 16 | 80 | -5 | 85 | 9.6184
IR | IR4B3139P | 16 | 80 | 0 | 80 | 10.3716
IR | IR4B3139P | 16 | 80 | 5 | 75 | 11.1949
IR | IR4B3139P | 16 | 80 | 10 | 70 | 12.0993
IR | IR4B3139P | 16 | 80 | 15 | 65 | 13.0973
IR | IR4B3139P | 16 | 80 | 20 | 60 | 14.2043
IR | IR4B3139P | 16 | 80 | 30 | 50 | 16.8211
IR | IR4B3139P | 16 | 90 | -30 | 120 | 5.8542
IR | IR4B3139P | 16 | 90 | -25 | 115 | 6.3081
IR | IR4B3139P | 16 | 90 | -20 | 110 | 6.7803
IR | IR4B3139P | 16 | 90 | -15 | 105 | 7.2786
IR | IR4B3139P | 16 | 90 | -10 | 100 | 7.8095
IR | IR4B3139P | 16 | 90 | -5 | 95 | 8.379
IR | IR4B3139P | 16 | 90 | 0 | 90 | 8.9925
IR | IR4B3139P | 16 | 90 | 5 | 85 | 9.6564
IR | IR4B3139P | 16 | 90 | 10 | 80 | 10.3793
IR | IR4B3139P | 16 | 90 | 15 | 75 | 11.1694
IR | IR4B3139P | 16 | 90 | 20 | 70 | 12.0359
IR | IR4B3139P | 16 | 90 | 30 | 60 | 14.0499
IR | IR4B3139P | 16 | 100 | -30 | 130 | 5.1781
IR | IR4B3139P | 16 | 100 | -25 | 125 | 5.569
IR | IR4B3139P | 16 | 100 | -20 | 120 | 5.9705
IR | IR4B3139P | 16 | 100 | -15 | 115 | 6.3906
IR | IR4B3139P | 16 | 100 | -10 | 110 | 6.8337
IR | IR4B3139P | 16 | 100 | -5 | 105 | 7.3051
IR | IR4B3139P | 16 | 100 | 0 | 100 | 7.8084
IR | IR4B3139P | 16 | 100 | 5 | 95 | 8.3499
IR | IR4B3139P | 16 | 100 | 10 | 90 | 8.9337
IR | IR4B3139P | 16 | 100 | 15 | 85 | 9.5662
IR | IR4B3139P | 16 | 100 | 20 | 80 | 10.254
IR | IR4B3139P | 16 | 100 | 30 | 70 | 11.8292
IR | IR4B3139P | 16 | 110 | -30 | 140 | 4.5414
IR | IR4B3139P | 16 | 110 | -25 | 135 | 4.8791
IR | IR4B3139P | 16 | 110 | -20 | 130 | 5.2226
IR | IR4B3139P | 16 | 110 | -15 | 125 | 5.5778
IR | IR4B3139P | 16 | 110 | -10 | 120 | 5.95
IR | IR4B3139P | 16 | 110 | -5 | 115 | 6.342
IR | IR4B3139P | 16 | 110 | 0 | 110 | 6.7583
IR | IR4B3139P | 16 | 110 | 5 | 105 | 7.2017
IR | IR4B3139P | 16 | 110 | 10 | 100 | 7.6766
IR | IR4B3139P | 16 | 110 | 15 | 95 | 8.1874
IR | IR4B3139P | 16 | 110 | 20 | 90 | 8.7381
IR | IR4B3139P | 16 | 110 | 30 | 80 | 9.9824
IR | IR4B3604P | 19 | 70 | -30 | 100 | 7.4119
IR | IR4B3604P | 19 | 70 | -25 | 95 | 8.0235
IR | IR4B3604P | 19 | 70 | -20 | 90 | 8.6747
IR | IR4B3604P | 19 | 70 | -15 | 85 | 9.374
IR | IR4B3604P | 19 | 70 | -10 | 80 | 10.1335
IR | IR4B3604P | 19 | 70 | -5 | 75 | 10.9615
IR | IR4B3604P | 19 | 70 | 0 | 70 | 11.8701
IR | IR4B3604P | 19 | 70 | 5 | 65 | 12.8731
IR | IR4B3604P | 19 | 70 | 10 | 60 | 13.9852
IR | IR4B3604P | 19 | 70 | 15 | 55 | 15.2271
IR | IR4B3604P | 19 | 70 | 20 | 50 | 16.6207
IR | IR4B3604P | 19 | 70 | 30 | 40 | 19.9889
IR | IR4B3604P | 19 | 80 | -30 | 110 | 6.5383
IR | IR4B3604P | 19 | 80 | -25 | 105 | 7.0676
IR | IR4B3604P | 19 | 80 | -20 | 100 | 7.6203
IR | IR4B3604P | 19 | 80 | -15 | 95 | 8.2052
IR | IR4B3604P | 19 | 80 | -10 | 90 | 8.8297
IR | IR4B3604P | 19 | 80 | -5 | 85 | 9.5019
IR | IR4B3604P | 19 | 80 | 0 | 80 | 10.2287
IR | IR4B3604P | 19 | 80 | 5 | 75 | 11.0203
IR | IR4B3604P | 19 | 80 | 10 | 70 | 11.886
IR | IR4B3604P | 19 | 80 | 15 | 65 | 12.8383
IR | IR4B3604P | 19 | 80 | 20 | 60 | 13.8905
IR | IR4B3604P | 19 | 80 | 30 | 50 | 16.3695
IR | IR4B3604P | 19 | 90 | -30 | 120 | 5.7779
IR | IR4B3604P | 19 | 90 | -25 | 115 | 6.2428
IR | IR4B3604P | 19 | 90 | -20 | 110 | 6.7195
IR | IR4B3604P | 19 | 90 | -15 | 105 | 7.2153
IR | IR4B3604P | 19 | 90 | -10 | 100 | 7.7383
IR | IR4B3604P | 19 | 90 | -5 | 95 | 8.2927
IR | IR4B3604P | 19 | 90 | 0 | 90 | 8.8855
IR | IR4B3604P | 19 | 90 | 5 | 85 | 9.5227
IR | IR4B3604P | 19 | 90 | 10 | 80 | 10.2114
IR | IR4B3604P | 19 | 90 | 15 | 75 | 10.9594
IR | IR4B3604P | 19 | 90 | 20 | 70 | 11.7763
IR | IR4B3604P | 19 | 90 | 30 | 60 | 13.661
IR | IR4B3604P | 19 | 100 | -30 | 130 | 5.083
IR | IR4B3604P | 19 | 100 | -25 | 125 | 5.4968
IR | IR4B3604P | 19 | 100 | -20 | 120 | 5.9138
IR | IR4B3604P | 19 | 100 | -15 | 115 | 6.3404
IR | IR4B3604P | 19 | 100 | -10 | 110 | 6.7838
IR | IR4B3604P | 19 | 100 | -5 | 105 | 7.2479
IR | IR4B3604P | 19 | 100 | 0 | 100 | 7.7382
IR | IR4B3604P | 19 | 100 | 5 | 95 | 8.2588
IR | IR4B3604P | 19 | 100 | 10 | 90 | 8.8156
IR | IR4B3604P | 19 | 100 | 15 | 85 | 9.414
IR | IR4B3604P | 19 | 100 | 20 | 80 | 10.0602
IR | IR4B3604P | 19 | 100 | 30 | 70 | 11.526
IR | IR4B3604P | 19 | 110 | -30 | 140 | 4.4239
IR | IR4B3604P | 19 | 110 | -25 | 135 | 4.7957
IR | IR4B3604P | 19 | 110 | -20 | 130 | 5.1641
IR | IR4B3604P | 19 | 110 | -15 | 125 | 5.5355
IR | IR4B3604P | 19 | 110 | -10 | 120 | 5.9156
IR | IR4B3604P | 19 | 110 | -5 | 115 | 6.3087
IR | IR4B3604P | 19 | 110 | 0 | 110 | 6.7187
IR | IR4B3604P | 19 | 110 | 5 | 105 | 7.1499
IR | IR4B3604P | 19 | 110 | 10 | 100 | 7.6055
IR | IR4B3604P | 19 | 110 | 15 | 95 | 8.0904
IR | IR4B3604P | 19 | 110 | 20 | 90 | 8.6088
IR | IR4B3604P | 19 | 110 | 30 | 80 | 9.7662
IR | IR6B4060P | 22 | 70 | -30 | 100 | 7.878
IR | IR6B4060P | 22 | 70 | -25 | 95 | 8.5145
IR | IR6B4060P | 22 | 70 | -20 | 90 | 8.6145
IR | IR6B4060P | 22 | 70 | -15 | 85 | 9.3759
IR | IR6B4060P | 22 | 70 | -10 | 80 | 10.1984
IR | IR6B4060P | 22 | 70 | -5 | 75 | 11.0925
IR | IR6B4060P | 22 | 70 | 0 | 70 | 12.0708
IR | IR6B4060P | 22 | 70 | 5 | 65 | 13.1457
IR | IR6B4060P | 22 | 70 | 10 | 60 | 14.3339
IR | IR6B4060P | 22 | 70 | 15 | 55 | 15.6543
IR | IR6B4060P | 22 | 70 | 20 | 50 | 17.1291
IR | IR6B4060P | 22 | 70 | 30 | 40 | 20.663
IR | IR6B4060P | 22 | 80 | -30 | 110 | 6.869
IR | IR6B4060P | 22 | 80 | -25 | 105 | 7.3975
IR | IR6B4060P | 22 | 80 | -20 | 100 | 7.6321
IR | IR6B4060P | 22 | 80 | -15 | 95 | 8.2555
IR | IR6B4060P | 22 | 80 | -10 | 90 | 8.9242
IR | IR6B4060P | 22 | 80 | -5 | 85 | 9.6467
IR | IR6B4060P | 22 | 80 | 0 | 80 | 10.4302
IR | IR6B4060P | 22 | 80 | 5 | 75 | 11.2838
IR | IR6B4060P | 22 | 80 | 10 | 70 | 12.2192
IR | IR6B4060P | 22 | 80 | 15 | 65 | 13.2476
IR | IR6B4060P | 22 | 80 | 20 | 60 | 14.3842
IR | IR6B4060P | 22 | 80 | 30 | 50 | 17.0558
IR | IR6B4060P | 22 | 90 | -30 | 120 | 6.0775
IR | IR6B4060P | 22 | 90 | -25 | 115 | 6.5254
IR | IR6B4060P | 22 | 90 | -20 | 110 | 6.7708
IR | IR6B4060P | 22 | 90 | -15 | 105 | 7.2856
IR | IR6B4060P | 22 | 90 | -10 | 100 | 7.8354
IR | IR6B4060P | 22 | 90 | -5 | 95 | 8.4253
IR | IR6B4060P | 22 | 90 | 0 | 90 | 9.0609
IR | IR6B4060P | 22 | 90 | 5 | 85 | 9.7493
IR | IR6B4060P | 22 | 90 | 10 | 80 | 10.498
IR | IR6B4060P | 22 | 90 | 15 | 75 | 11.3138
IR | IR6B4060P | 22 | 90 | 20 | 70 | 12.2081
IR | IR6B4060P | 22 | 90 | 30 | 60 | 14.2771
IR | IR6B4060P | 22 | 100 | -30 | 130 | 5.3992
IR | IR6B4060P | 22 | 100 | -25 | 125 | 5.783
IR | IR6B4060P | 22 | 100 | -20 | 120 | 5.9662
IR | IR6B4060P | 22 | 100 | -15 | 115 | 6.3955
IR | IR6B4060P | 22 | 100 | -10 | 110 | 6.8518
IR | IR6B4060P | 22 | 100 | -5 | 105 | 7.339
IR | IR6B4060P | 22 | 100 | 0 | 100 | 7.8686
IR | IR6B4060P | 22 | 100 | 5 | 95 | 8.4225
IR | IR6B4060P | 22 | 100 | 10 | 90 | 9.0292
IR | IR6B4060P | 22 | 100 | 15 | 85 | 9.6861
IR | IR6B4060P | 22 | 100 | 20 | 80 | 10.4001
IR | IR6B4060P | 22 | 100 | 30 | 70 | 12.0311
IR | IR6B4060P | 22 | 110 | -30 | 140 | 4.7665
IR | IR6B4060P | 22 | 110 | -25 | 135 | 5.0986
IR | IR6B4060P | 22 | 110 | -20 | 130 | 5.193
IR | IR6B4060P | 22 | 110 | -15 | 125 | 5.5545
IR | IR6B4060P | 22 | 110 | -10 | 120 | 5.9368
IR | IR6B4060P | 22 | 110 | -5 | 115 | 6.3424
IR | IR6B4060P | 22 | 110 | 0 | 110 | 6.7748
IR | IR6B4060P | 22 | 110 | 5 | 105 | 7.2369
IR | IR6B4060P | 22 | 110 | 10 | 100 | 7.733
IR | IR6B4060P | 22 | 110 | 15 | 95 | 8.2667
IR | IR6B4060P | 22 | 110 | 20 | 90 | 8.8427
IR | IR6B4060P | 22 | 110 | 30 | 80 | 10.143
Copeland | 3DB3R12ML-TFD | 7.5 | 110 | 10 | 100 | 7.9
Copeland | 3DB3R12ML-TFD | 7.5 | 110 | 15 | 95 | 8.4
Copeland | 3DB3R12ML-TFD | 7.5 | 110 | 20 | 90 | 9.1
Copeland | 3DB3R12ML-TFD | 7.5 | 110 | 25 | 85 | 9.8
Copeland | 3DB3R12ML-TFD | 7.5 | 110 | 30 | 80 | 10.5
Copeland | 3DB3R12ML-TFD | 7.5 | 110 | 35 | 75 | 11.4
Copeland | 3DB3R12ML-TFD | 7.5 | 100 | 10 | 90 | 9.2
Copeland | 3DB3R12ML-TFD | 7.5 | 100 | 15 | 85 | 9.9
Copeland | 3DB3R12ML-TFD | 7.5 | 100 | 20 | 80 | 10.7
Copeland | 3DB3R12ML-TFD | 7.5 | 100 | 25 | 75 | 11.6
Copeland | 3DB3R12ML-TFD | 7.5 | 100 | 30 | 70 | 12.5
Copeland | 3DB3R12ML-TFD | 7.5 | 100 | 35 | 65 | 13.6
Copeland | 3DB3R12ML-TFD | 7.5 | 90 | 10 | 80 | 10.7
Copeland | 3DB3R12ML-TFD | 7.5 | 90 | 15 | 75 | 11.6
Copeland | 3DB3R12ML-TFD | 7.5 | 90 | 20 | 70 | 12.6
Copeland | 3DB3R12ML-TFD | 7.5 | 90 | 25 | 65 | 13.7
Copeland | 3DB3R12ML-TFD | 7.5 | 90 | 30 | 60 | 15
Copeland | 3DB3R12ML-TFD | 7.5 | 90 | 35 | 55 | 16.4
Copeland | 3DB3R12ML-TFD | 7.5 | 70 | 10 | 60 | 14.6
Copeland | 3DB3R12ML-TFD | 7.5 | 70 | 15 | 55 | 16.1
Copeland | 3DB3R12ML-TFD | 7.5 | 70 | 20 | 50 | 17.8
Copeland | 3DB3R12ML-TFD | 7.5 | 70 | 25 | 45 | 19.7
Copeland | 3DB3R12ML-TFD | 7.5 | 70 | 30 | 40 | 21.9
Copeland | 3DB3R12ML-TFD | 7.5 | 70 | 35 | 35 | 24.4
Copeland | 2DL3F20KL-TFD | 3.5 | 110 | -30 | 140 | 4.5
Copeland | 2DL3F20KL-TFD | 3.5 | 110 | -25 | 135 | 4.9
Copeland | 2DL3F20KL-TFD | 3.5 | 110 | -20 | 130 | 5.3
Copeland | 2DL3F20KL-TFD | 3.5 | 110 | -15 | 125 | 5.6
Copeland | 2DL3F20KL-TFD | 3.5 | 110 | -10 | 120 | 6.1
Copeland | 2DL3F20KL-TFD | 3.5 | 110 | -5 | 115 | 6.5
Copeland | 2DL3F20KL-TFD | 3.5 | 105 | -30 | 135 | 4.9
Copeland | 2DL3F20KL-TFD | 3.5 | 105 | -25 | 130 | 5.2
Copeland | 2DL3F20KL-TFD | 3.5 | 105 | -20 | 125 | 5.6
Copeland | 2DL3F20KL-TFD | 3.5 | 105 | -15 | 120 | 6.1
Copeland | 2DL3F20KL-TFD | 3.5 | 105 | -10 | 115 | 6.5
Copeland | 2DL3F20KL-TFD | 3.5 | 105 | -5 | 110 | 7
Copeland | 2DL3F20KL-TFD | 3.5 | 100 | -30 | 130 | 5.2
Copeland | 2DL3F20KL-TFD | 3.5 | 100 | -25 | 125 | 5.6
Copeland | 2DL3F20KL-TFD | 3.5 | 100 | -20 | 120 | 6
Copeland | 2DL3F20KL-TFD | 3.5 | 100 | -15 | 115 | 6.5
Copeland | 2DL3F20KL-TFD | 3.5 | 100 | -10 | 110 | 7
Copeland | 2DL3F20KL-TFD | 3.5 | 100 | -5 | 105 | 7.5
Copeland | 2DL3F20KL-TFD | 3.5 | 80 | -30 | 110 | 6.7
Copeland | 2DL3F20KL-TFD | 3.5 | 80 | -25 | 105 | 7.3
Copeland | 2DL3F20KL-TFD | 3.5 | 80 | -20 | 100 | 7.9
Copeland | 2DL3F20KL-TFD | 3.5 | 80 | -15 | 95 | 8.6
Copeland | 2DL3F20KL-TFD | 3.5 | 80 | -10 | 90 | 9.3
Copeland | 2DL3F20KL-TFD | 3.5 | 80 | -5 | 85 | 10
Copeland | 2DL3F20KL-TFD | 3.5 | 70 | -30 | 100 | 7.6
Copeland | 2DL3F20KL-TFD | 3.5 | 70 | -25 | 95 | 8.3
Copeland | 2DL3F20KL-TFD | 3.5 | 70 | -20 | 90 | 9
Copeland | 2DL3F20KL-TFD | 3.5 | 70 | -15 | 85 | 9.8
Copeland | 2DL3F20KL-TFD | 3.5 | 70 | -10 | 80 | 10.7
Copeland | 2DL3F20KL-TFD | 3.5 | 70 | -5 | 75 | 11.6
Copeland | 6DL3F93KE-TSK | 15 | 110 | -30 | 140 | 4.6
Copeland | 6DL3F93KE-TSK | 15 | 110 | -25 | 135 | 5
Copeland | 6DL3F93KE-TSK | 15 | 110 | -20 | 130 | 5.3
Copeland | 6DL3F93KE-TSK | 15 | 110 | -15 | 125 | 5.7
Copeland | 6DL3F93KE-TSK | 15 | 110 | -10 | 120 | 6.1
Copeland | 6DL3F93KE-TSK | 15 | 110 | -5 | 115 | 6.5
Copeland | 6DL3F93KE-TSK | 15 | 105 | -30 | 135 | 4.9
Copeland | 6DL3F93KE-TSK | 15 | 105 | -25 | 130 | 5.3
Copeland | 6DL3F93KE-TSK | 15 | 105 | -20 | 125 | 5.7
Copeland | 6DL3F93KE-TSK | 15 | 105 | -15 | 120 | 6.1
Copeland | 6DL3F93KE-TSK | 15 | 105 | -10 | 115 | 6.5
Copeland | 6DL3F93KE-TSK | 15 | 105 | -5 | 110 | 7
Copeland | 6DL3F93KE-TSK | 15 | 100 | -30 | 130 | 5.3
Copeland | 6DL3F93KE-TSK | 15 | 100 | -25 | 125 | 5.7
Copeland | 6DL3F93KE-TSK | 15 | 100 | -20 | 120 | 6.1
Copeland | 6DL3F93KE-TSK | 15 | 100 | -15 | 115 | 6.6
Copeland | 6DL3F93KE-TSK | 15 | 100 | -10 | 110 | 7.1
Copeland | 6DL3F93KE-TSK | 15 | 100 | -5 | 105 | 7.5
Copeland | 6DL3F93KE-TSK | 15 | 80 | -30 | 110 | 7.1
Copeland | 6DL3F93KE-TSK | 15 | 80 | -25 | 105 | 7.6
Copeland | 6DL3F93KE-TSK | 15 | 80 | -20 | 100 | 8.2
Copeland | 6DL3F93KE-TSK | 15 | 80 | -15 | 95 | 8.8
Copeland | 6DL3F93KE-TSK | 15 | 80 | -10 | 90 | 9.5
Copeland | 6DL3F93KE-TSK | 15 | 80 | -5 | 85 | 10.1
Copeland | 6DL3F93KE-TSK | 15 | 70 | -30 | 100 | 8.2
Copeland | 6DL3F93KE-TSK | 15 | 70 | -25 | 95 | 8.8
Copeland | 6DL3F93KE-TSK | 15 | 70 | -20 | 90 | 9.5
Copeland | 6DL3F93KE-TSK | 15 | 70 | -15 | 85 | 10.1
Copeland | 6DL3F93KE-TSK | 15 | 70 | -10 | 80 | 10.8
Copeland | 6DL3F93KE-TSK | 15 | 70 | -5 | 75 | 11.5
Copeland | 2DD3R63KL-TFD |  | 110 | 10 | 100 | 8.1
Copeland | 2DD3R63KL-TFD |  | 110 | 15 | 95 | 8.7
Copeland | 2DD3R63KL-TFD |  | 110 | 20 | 90 | 9.4
Copeland | 2DD3R63KL-TFD |  | 110 | 25 | 85 | 10.2
Copeland | 2DD3R63KL-TFD |  | 110 | 30 | 80 | 11
Copeland | 2DD3R63KL-TFD |  | 110 | 35 | 75 | 12
Copeland | 2DD3R63KL-TFD |  | 100 | 10 | 90 | 9.4
Copeland | 2DD3R63KL-TFD |  | 100 | 15 | 85 | 10.2
Copeland | 2DD3R63KL-TFD |  | 100 | 20 | 80 | 11.1
Copeland | 2DD3R63KL-TFD |  | 100 | 25 | 75 | 12.1
Copeland | 2DD3R63KL-TFD |  | 100 | 30 | 70 | 13.2
Copeland | 2DD3R63KL-TFD |  | 100 | 35 | 65 | 14.4
Copeland | 2DD3R63KL-TFD |  | 90 | 10 | 80 | 11.1
Copeland | 2DD3R63KL-TFD |  | 90 | 15 | 75 | 12.1
Copeland | 2DD3R63KL-TFD |  | 90 | 20 | 70 | 13.2
Copeland | 2DD3R63KL-TFD |  | 90 | 25 | 65 | 14.4
Copeland | 2DD3R63KL-TFD |  | 90 | 30 | 60 | 15.9
Copeland | 2DD3R63KL-TFD |  | 90 | 35 | 55 | 17.5
Copeland | 2DD3R63KL-TFD |  | 70 | 10 | 60 | 15.2
Copeland | 2DD3R63KL-TFD |  | 70 | 15 | 55 | 16.8
Copeland | 2DD3R63KL-TFD |  | 70 | 20 | 50 | 18.7
Copeland | 2DD3R63KL-TFD |  | 70 | 25 | 45 | 20.9
Copeland | 2DD3R63KL-TFD |  | 70 | 30 | 40 | 23.5
Copeland | 2DD3R63KL-TFD |  | 70 | 35 | 35 | 26.7
Copeland | 4DB3R20ML-TSK | 13.5 | 110 | 10 | 100 | 7.7
Copeland | 4DB3R20ML-TSK | 13.5 | 110 | 15 | 95 | 8.3
Copeland | 4DB3R20ML-TSK | 13.5 | 110 | 20 | 90 | 8.9
Copeland | 4DB3R20ML-TSK | 13.5 | 110 | 25 | 85 | 9.6
Copeland | 4DB3R20ML-TSK | 13.5 | 110 | 30 | 80 | 10.3
Copeland | 4DB3R20ML-TSK | 13.5 | 110 | 35 | 75 | 11
Copeland | 4DB3R20ML-TSK | 13.5 | 100 | 10 | 90 | 9
Copeland | 4DB3R20ML-TSK | 13.5 | 100 | 15 | 85 | 9.8
Copeland | 4DB3R20ML-TSK | 13.5 | 100 | 20 | 80 | 10.6
Copeland | 4DB3R20ML-TSK | 13.5 | 100 | 25 | 75 | 11.4
Copeland | 4DB3R20ML-TSK | 13.5 | 100 | 30 | 70 | 12.3
Copeland | 4DB3R20ML-TSK | 13.5 | 100 | 35 | 65 | 13.3
Copeland | 4DB3R20ML-TSK | 13.5 | 90 | 10 | 80 | 10.6
Copeland | 4DB3R20ML-TSK | 13.5 | 90 | 15 | 75 | 11.6
Copeland | 4DB3R20ML-TSK | 13.5 | 90 | 20 | 70 | 12.6
Copeland | 4DB3R20ML-TSK | 13.5 | 90 | 25 | 65 | 13.7
Copeland | 4DB3R20ML-TSK | 13.5 | 90 | 30 | 60 | 14.9
Copeland | 4DB3R20ML-TSK | 13.5 | 90 | 35 | 55 | 16.1
Copeland | 4DB3R20ML-TSK | 13.5 | 70 | 10 | 60 | 15.1
Copeland | 4DB3R20ML-TSK | 13.5 | 70 | 15 | 55 | 16.7
Copeland | 4DB3R20ML-TSK | 13.5 | 70 | 20 | 50 | 18.5
Copeland | 4DB3R20ML-TSK | 13.5 | 70 | 25 | 45 | 20.4
Copeland | 4DB3R20ML-TSK | 13.5 | 70 | 30 | 40 | 22.6
Copeland | 4DB3R20ML-TSK | 13.5 | 70 | 35 | 35 | 25.1
Copeland | 4DJ3F76KE-TSK |  | 110 | -30 | 140 | 4.7
Copeland | 4DJ3F76KE-TSK |  | 110 | -25 | 135 | 5.1
Copeland | 4DJ3F76KE-TSK |  | 110 | -20 | 130 | 5.4
Copeland | 4DJ3F76KE-TSK |  | 110 | -15 | 125 | 5.7
Copeland | 4DJ3F76KE-TSK |  | 110 | -10 | 120 | 6.1
Copeland | 4DJ3F76KE-TSK |  | 110 | -5 | 115 | 6.4
Copeland | 4DJ3F76KE-TSK |  | 105 | -30 | 135 | 5.1
Copeland | 4DJ3F76KE-TSK |  | 105 | -25 | 130 | 5.4
Copeland | 4DJ3F76KE-TSK |  | 105 | -20 | 125 | 5.8
Copeland | 4DJ3F76KE-TSK |  | 105 | -15 | 120 | 6.1
Copeland | 4DJ3F76KE-TSK |  | 105 | -10 | 115 | 6.5
Copeland | 4DJ3F76KE-TSK |  | 105 | -5 | 110 | 6.9
Copeland | 4DJ3F76KE-TSK |  | 100 | -30 | 130 | 5.4
Copeland | 4DJ3F76KE-TSK |  | 100 | -25 | 125 | 5.8
Copeland | 4DJ3F76KE-TSK |  | 100 | -20 | 120 | 6.2
Copeland | 4DJ3F76KE-TSK |  | 100 | -15 | 115 | 6.6
Copeland | 4DJ3F76KE-TSK |  | 100 | -10 | 110 | 7.1
Copeland | 4DJ3F76KE-TSK |  | 100 | -5 | 105 | 7.5
Copeland | 4DJ3F76KE-TSK |  | 80 | -30 | 110 | 7.1
Copeland | 4DJ3F76KE-TSK |  | 80 | -25 | 105 | 7.7
Copeland | 4DJ3F76KE-TSK |  | 80 | -20 | 100 | 8.3
Copeland | 4DJ3F76KE-TSK |  | 80 | -15 | 95 | 8.9
Copeland | 4DJ3F76KE-TSK |  | 80 | -10 | 90 | 9.5
Copeland | 4DJ3F76KE-TSK |  | 80 | -5 | 85 | 10.2
Copeland | 4DJ3F76KE-TSK |  | 70 | -30 | 100 | 8.1
Copeland | 4DJ3F76KE-TSK |  | 70 | -25 | 95 | 8.8
Copeland | 4DJ3F76KE-TSK |  | 70 | -20 | 90 | 9.5
Copeland | 4DJ3F76KE-TSK |  | 70 | -15 | 85 | 10.3
Copeland | 4DJ3F76KE-TSK |  | 70 | -10 | 80 | 11
Copeland | 4DJ3F76KE-TSK |  | 70 | -5 | 75 | 11.8
Copeland | 4DL3F63KE-TSK |  | 110 | -30 | 140 | 4.6
Copeland | 4DL3F63KE-TSK |  | 110 | -25 | 135 | 4.9
Copeland | 4DL3F63KE-TSK |  | 110 | -20 | 130 | 5.2
Copeland | 4DL3F63KE-TSK |  | 110 | -15 | 125 | 5.6
Copeland | 4DL3F63KE-TSK |  | 110 | -10 | 120 | 6
Copeland | 4DL3F63KE-TSK |  | 110 | -5 | 115 | 6.4
Copeland | 4DL3F63KE-TSK |  | 105 | -30 | 135 | 4.9
Copeland | 4DL3F63KE-TSK |  | 105 | -25 | 130 | 5.3
Copeland | 4DL3F63KE-TSK |  | 105 | -20 | 125 | 5.6
Copeland | 4DL3F63KE-TSK |  | 105 | -15 | 120 | 6
Copeland | 4DL3F63KE-TSK |  | 105 | -10 | 115 | 6.5
Copeland | 4DL3F63KE-TSK |  | 105 | -5 | 110 | 6.9
Copeland | 4DL3F63KE-TSK |  | 100 | -30 | 130 | 5.3
Copeland | 4DL3F63KE-TSK |  | 100 | -25 | 125 | 5.7
Copeland | 4DL3F63KE-TSK |  | 100 | -20 | 120 | 6.1
Copeland | 4DL3F63KE-TSK |  | 100 | -15 | 115 | 6.5
Copeland | 4DL3F63KE-TSK |  | 100 | -10 | 110 | 7
Copeland | 4DL3F63KE-TSK |  | 100 | -5 | 105 | 7.4
Copeland | 4DL3F63KE-TSK |  | 80 | -30 | 110 | 7.1
Copeland | 4DL3F63KE-TSK |  | 80 | -25 | 105 | 7.6
Copeland | 4DL3F63KE-TSK |  | 80 | -20 | 100 | 8.1
Copeland | 4DL3F63KE-TSK |  | 80 | -15 | 95 | 8.7
Copeland | 4DL3F63KE-TSK |  | 80 | -10 | 90 | 9.3
Copeland | 4DL3F63KE-TSK |  | 80 | -5 | 85 | 10
Copeland | 4DL3F63KE-TSK |  | 70 | -30 | 100 | 8.2
Copeland | 4DL3F63KE-TSK |  | 70 | -25 | 95 | 8.8
Copeland | 4DL3F63KE-TSK |  | 70 | -20 | 90 | 9.4
Copeland | 4DL3F63KE-TSK |  | 70 | -15 | 85 | 10
Copeland | 4DL3F63KE-TSK |  | 70 | -10 | 80 | 10.7
Copeland | 4DL3F63KE-TSK |  | 70 | -5 | 75 | 11.4
Copeland | 3DS3F46KE-TFD |  | 110 | -30 | 140 | 4.8
Copeland | 3DS3F46KE-TFD |  | 110 | -25 | 135 | 5
Copeland | 3DS3F46KE-TFD |  | 110 | -20 | 130 | 5.3
Copeland | 3DS3F46KE-TFD |  | 110 | -15 | 125 | 5.7
Copeland | 3DS3F46KE-TFD |  | 110 | -10 | 120 | 6
Copeland | 3DS3F46KE-TFD |  | 110 | -5 | 115 | 6.4
Copeland | 3DS3F46KE-TFD |  | 105 | -30 | 135 | 5
Copeland | 3DS3F46KE-TFD |  | 105 | -25 | 130 | 5.4
Copeland | 3DS3F46KE-TFD |  | 105 | -20 | 125 | 5.7
Copeland | 3DS3F46KE-TFD |  | 105 | -15 | 120 | 6
Copeland | 3DS3F46KE-TFD |  | 105 | -10 | 115 | 6.4
Copeland | 3DS3F46KE-TFD |  | 105 | -5 | 110 | 6.8
Copeland | 3DS3F46KE-TFD |  | 100 | -30 | 130 | 5.3
Copeland | 3DS3F46KE-TFD |  | 100 | -25 | 125 | 5.7
Copeland | 3DS3F46KE-TFD |  | 100 | -20 | 120 | 6
Copeland | 3DS3F46KE-TFD |  | 100 | -15 | 115 | 6.4
Copeland | 3DS3F46KE-TFD |  | 100 | -10 | 110 | 6.8
Copeland | 3DS3F46KE-TFD |  | 100 | -5 | 105 | 7.3
Copeland | 3DS3F46KE-TFD |  | 80 | -30 | 110 | 6.6
Copeland | 3DS3F46KE-TFD |  | 80 | -25 | 105 | 7.1
Copeland | 3DS3F46KE-TFD |  | 80 | -20 | 100 | 7.7
Copeland | 3DS3F46KE-TFD |  | 80 | -15 | 95 | 8.2
Copeland | 3DS3F46KE-TFD |  | 80 | -10 | 90 | 8.8
Copeland | 3DS3F46KE-TFD |  | 80 | -5 | 85 | 9.5
Copeland | 3DS3F46KE-TFD |  | 70 | -30 | 100 | 7.4
Copeland | 3DS3F46KE-TFD |  | 70 | -25 | 95 | 8
Copeland | 3DS3F46KE-TFD |  | 70 | -20 | 90 | 8.7
Copeland | 3DS3F46KE-TFD |  | 70 | -15 | 85 | 9.4
Copeland | 3DS3F46KE-TFD |  | 70 | -10 | 80 | 10.1
Copeland | 3DS3F46KE-TFD |  | 70 | -5 | 75 | 10.9
Copeland | 3DB3A075L-TFD |  | 110 | -30 | 140 | 4.6
Copeland | 3DB3A075L-TFD |  | 110 | -25 | 135 | 4.9
Copeland | 3DB3A075L-TFD |  | 110 | -20 | 130 | 5.2
Copeland | 3DB3A075L-TFD |  | 110 | -15 | 125 | 5.6
Copeland | 3DB3A075L-TFD |  | 110 | -10 | 120 | 6
Copeland | 3DB3A075L-TFD |  | 110 | -5 | 115 | 6.4
Copeland | 3DB3A075L-TFD |  | 105 | -30 | 135 | 4.9
Copeland | 3DB3A075L-TFD |  | 105 | -25 | 130 | 5.2
Copeland | 3DB3A075L-TFD |  | 105 | -20 | 125 | 5.6
Copeland | 3DB3A075L-TFD |  | 105 | -15 | 120 | 6
Copeland | 3DB3A075L-TFD |  | 105 | -10 | 115 | 6.4
Copeland | 3DB3A075L-TFD |  | 105 | -5 | 110 | 6.9
Copeland | 3DB3A075L-TFD |  | 100 | -30 | 130 | 5.2
Copeland | 3DB3A075L-TFD |  | 100 | -25 | 125 | 5.6
Copeland | 3DB3A075L-TFD |  | 100 | -20 | 120 | 6
Copeland | 3DB3A075L-TFD |  | 100 | -15 | 115 | 6.4
Copeland | 3DB3A075L-TFD |  | 100 | -10 | 110 | 6.9
Copeland | 3DB3A075L-TFD |  | 100 | -5 | 105 | 7.4
Copeland | 3DB3A075L-TFD |  | 80 | -30 | 110 | 6.6
Copeland | 3DB3A075L-TFD |  | 80 | -25 | 105 | 7.2
Copeland | 3DB3A075L-TFD |  | 80 | -20 | 100 | 7.8
Copeland | 3DB3A075L-TFD |  | 80 | -15 | 95 | 8.4
Copeland | 3DB3A075L-TFD |  | 80 | -10 | 90 | 9.1
Copeland | 3DB3A075L-TFD |  | 80 | -5 | 85 | 9.9
Copeland | 3DB3A075L-TFD |  | 70 | -30 | 100 | 7.5
Copeland | 3DB3A075L-TFD |  | 70 | -25 | 95 | 8.1
Copeland | 3DB3A075L-TFD |  | 70 | -20 | 90 | 8.9
Copeland | 3DB3A075L-TFD |  | 70 | -15 | 85 | 9.7
Copeland | 3DB3A075L-TFD |  | 70 | -10 | 80 | 10.5
Copeland | 3DB3A075L-TFD |  | 70 | -5 | 75 | 11.4
Copeland | 6DL3F93KE-TSK |  | 110 | -30 | 140 | 4.6
Copeland | 6DL3F93KE-TSK |  | 110 | -25 | 135 | 5
Copeland | 6DL3F93KE-TSK |  | 110 | -20 | 130 | 5.3
Copeland | 6DL3F93KE-TSK |  | 110 | -15 | 125 | 5.7
Copeland | 6DL3F93KE-TSK |  | 110 | -10 | 120 | 6.1
Copeland | 6DL3F93KE-TSK |  | 110 | -5 | 115 | 6.5
Copeland | 6DL3F93KE-TSK |  | 105 | -30 | 135 | 4.9
Copeland | 6DL3F93KE-TSK |  | 105 | -25 | 130 | 5.3
Copeland | 6DL3F93KE-TSK |  | 105 | -20 | 125 | 5.7
Copeland | 6DL3F93KE-TSK |  | 105 | -15 | 120 | 6.1
Copeland | 6DL3F93KE-TSK |  | 105 | -10 | 115 | 6.5
Copeland | 6DL3F93KE-TSK |  | 105 | -5 | 110 | 7
Copeland | 6DL3F93KE-TSK |  | 100 | -30 | 130 | 5.3
Copeland | 6DL3F93KE-TSK |  | 100 | -25 | 125 | 5.7
Copeland | 6DL3F93KE-TSK |  | 100 | -20 | 120 | 6.1
Copeland | 6DL3F93KE-TSK |  | 100 | -15 | 115 | 6.6
Copeland | 6DL3F93KE-TSK |  | 100 | -10 | 110 | 7.1
Copeland | 6DL3F93KE-TSK |  | 100 | -5 | 105 | 7.5
Copeland | 6DL3F93KE-TSK |  | 80 | -30 | 110 | 7.1
Copeland | 6DL3F93KE-TSK |  | 80 | -25 | 105 | 7.6
Copeland | 6DL3F93KE-TSK |  | 80 | -20 | 100 | 8.2
Copeland | 6DL3F93KE-TSK |  | 80 | -15 | 95 | 8.8
Copeland | 6DL3F93KE-TSK |  | 80 | -10 | 90 | 9.5
Copeland | 6DL3F93KE-TSK |  | 80 | -5 | 85 | 10.1
Copeland | 6DL3F93KE-TSK |  | 70 | -30 | 100 | 8.2
Copeland | 6DL3F93KE-TSK |  | 70 | -25 | 95 | 8.8
Copeland | 6DL3F93KE-TSK |  | 70 | -20 | 90 | 9.5
Copeland | 6DL3F93KE-TSK |  | 70 | -15 | 85 | 10.1
Copeland | 6DL3F93KE-TSK |  | 70 | -10 | 80 | 10.8
Copeland | 6DL3F93KE-TSK |  | 70 | -5 | 75 | 11.5
Copeland | 3DF3F40KE-TFD |  | 110 | -30 | 140 | 4.7
Copeland | 3DF3F40KE-TFD |  | 110 | -25 | 135 | 5
Copeland | 3DF3F40KE-TFD |  | 110 | -20 | 130 | 5.3
Copeland | 3DF3F40KE-TFD |  | 110 | -15 | 125 | 5.7
Copeland | 3DF3F40KE-TFD |  | 110 | -10 | 120 | 6
Copeland | 3DF3F40KE-TFD |  | 110 | -5 | 115 | 6.4
Copeland | 3DF3F40KE-TFD |  | 105 | -30 | 135 | 5
Copeland | 3DF3F40KE-TFD |  | 105 | -25 | 130 | 5.3
Copeland | 3DF3F40KE-TFD |  | 105 | -20 | 125 | 5.7
Copeland | 3DF3F40KE-TFD |  | 105 | -15 | 120 | 6.1
Copeland | 3DF3F40KE-TFD |  | 105 | -10 | 115 | 6.5
Copeland | 3DF3F40KE-TFD |  | 105 | -5 | 110 | 6.9
Copeland | 3DF3F40KE-TFD |  | 100 | -30 | 130 | 5.3
Copeland | 3DF3F40KE-TFD |  | 100 | -25 | 125 | 5.7
Copeland | 3DF3F40KE-TFD |  | 100 | -20 | 120 | 6
Copeland | 3DF3F40KE-TFD |  | 100 | -15 | 115 | 6.5
Copeland | 3DF3F40KE-TFD |  | 100 | -10 | 110 | 6.9
Copeland | 3DF3F40KE-TFD |  | 100 | -5 | 105 | 7.4
Copeland | 3DF3F40KE-TFD |  | 80 | -30 | 110 | 6.7
Copeland | 3DF3F40KE-TFD |  | 80 | -25 | 105 | 7.3
Copeland | 3DF3F40KE-TFD |  | 80 | -20 | 100 | 7.8
Copeland | 3DF3F40KE-TFD |  | 80 | -15 | 95 | 8.4
Copeland | 3DF3F40KE-TFD |  | 80 | -10 | 90 | 9.1
Copeland | 3DF3F40KE-TFD |  | 80 | -5 | 85 | 9.8
Copeland | 3DF3F40KE-TFD |  | 70 | -30 | 100 | 7.6
Copeland | 3DF3F40KE-TFD |  | 70 | -25 | 95 | 8.2
Copeland | 3DF3F40KE-TFD |  | 70 | -20 | 90 | 8.9
Copeland | 3DF3F40KE-TFD |  | 70 | -15 | 85 | 9.6
Copeland | 3DF3F40KE-TFD |  | 70 | -10 | 80 | 10.4
Copeland | 3DF3F40KE-TFD |  | 70 | -5 | 75 | 11.2
Copeland | 4DL3A150L-TSK |  | 110 | -30 | 140 | 4.1
Copeland | 4DL3A150L-TSK |  | 110 | -25 | 135 | 4.5
Copeland | 4DL3A150L-TSK |  | 110 | -20 | 130 | 5
Copeland | 4DL3A150L-TSK |  | 110 | -15 | 125 | 5.4
Copeland | 4DL3A150L-TSK |  | 110 | -10 | 120 | 5.9
Copeland | 4DL3A150L-TSK |  | 110 | -5 | 115 | 6.4
Copeland | 4DL3A150L-TSK |  | 105 | -30 | 135 | 4.4
Copeland | 4DL3A150L-TSK |  | 105 | -25 | 130 | 4.9
Copeland | 4DL3A150L-TSK |  | 105 | -20 | 125 | 5.4
Copeland | 4DL3A150L-TSK |  | 105 | -15 | 120 | 5.9
Copeland | 4DL3A150L-TSK |  | 105 | -10 | 115 | 6.4
Copeland | 4DL3A150L-TSK |  | 105 | -5 | 110 | 6.9
Copeland | 4DL3A150L-TSK |  | 100 | -30 | 130 | 4.8
Copeland | 4DL3A150L-TSK |  | 100 | -25 | 125 | 5.9
Copeland | 4DL3A150L-TSK |  | 100 | -20 | 120 | 5.8
Copeland | 4DL3A150L-TSK |  | 100 | -15 | 115 | 6.3
Copeland | 4DL3A150L-TSK |  | 100 | -10 | 110 | 6.9
Copeland | 4DL3A150L-TSK |  | 100 | -5 | 105 | 7.4
Copeland | 4DL3A150L-TSK |  | 80 | -30 | 110 | 6.4
Copeland | 4DL3A150L-TSK |  | 80 | -25 | 105 | 7
Copeland | 4DL3A150L-TSK |  | 80 | -20 | 100 | 7.6
Copeland | 4DL3A150L-TSK |  | 80 | -15 | 95 | 8.2
Copeland | 4DL3A150L-TSK |  | 80 | -10 | 90 | 8.9
Copeland | 4DL3A150L-TSK |  | 80 | -5 | 85 | 9.6
Copeland | 4DL3A150L-TSK |  | 70 | -30 | 100 | 7.1
Copeland | 4DL3A150L-TSK |  | 70 | -25 | 95 | 7.7
Copeland | 4DL3A150L-TSK |  | 70 | -20 | 90 | 8.4
Copeland | 4DL3A150L-TSK |  | 70 | -15 | 85 | 9.1
Copeland | 4DL3A150L-TSK |  | 70 | -10 | 80 | 9.9
Copeland | 4DL3A150L-TSK |  | 70 | -5 | 75 | 10.7
Copeland | 4DH3-250E-TSK |  | 110 | 10 | 100 | 7.8
Copeland | 4DH3-250E-TSK |  | 110 | 15 | 95 | 8.4
Copeland | 4DH3-250E-TSK |  | 110 | 20 | 90 | 9
Copeland | 4DH3-250E-TSK |  | 110 | 25 | 85 | 9.7
Copeland | 4DH3-250E-TSK |  | 110 | 30 | 80 | 10.4
Copeland | 4DH3-250E-TSK |  | 110 | 35 | 75 | 11.1
Copeland | 4DH3-250E-TSK |  | 100 | 10 | 90 | 9.1
Copeland | 4DH3-250E-TSK |  | 100 | 15 | 85 | 9.9
Copeland | 4DH3-250E-TSK |  | 100 | 20 | 80 | 10.7
Copeland | 4DH3-250E-TSK |  | 100 | 25 | 75 | 11.5
Copeland | 4DH3-250E-TSK |  | 100 | 30 | 70 | 12.4
Copeland | 4DH3-250E-TSK |  | 100 | 35 | 65 | 13.3
Copeland | 4DH3-250E-TSK |  | 90 | 10 | 80 | 10.8
Copeland | 4DH3-250E-TSK |  | 90 | 15 | 75 | 11.7
Copeland | 4DH3-250E-TSK |  | 90 | 20 | 70 | 12.7
Copeland | 4DH3-250E-TSK |  | 90 | 25 | 65 | 13.8
Copeland | 4DH3-250E-TSK |  | 90 | 30 | 60 | 15
Copeland | 4DH3-250E-TSK |  | 90 | 35 | 55 | 16.3
Copeland | 4DH3-250E-TSK |  | 70 | 10 | 60 | 15.5
Copeland | 4DH3-250E-TSK |  | 70 | 15 | 55 | 17.2
Copeland | 4DH3-250E-TSK |  | 70 | 20 | 50 | 19
Copeland | 4DH3-250E-TSK |  | 70 | 25 | 45 | 21
Copeland | 4DH3-250E-TSK |  | 70 | 30 | 40 | 23.3
Copeland | 4DH3-250E-TSK |  | 70 | 35 | 35 | 25.9
Copeland | 3DB3A100L-TFD |  | 110 | 10 | 100 | 7.9
Copeland | 3DB3A100L-TFD |  | 110 | 15 | 95 | 8.4
Copeland | 3DB3A100L-TFD |  | 110 | 20 | 90 | 9.1
Copeland | 3DB3A100L-TFD |  | 110 | 25 | 85 | 9.8
Copeland | 3DB3A100L-TFD |  | 110 | 30 | 80 | 10.5
Copeland | 3DB3A100L-TFD |  | 110 | 35 | 75 | 11.4
Copeland | 3DB3A100L-TFD |  | 100 | 10 | 90 | 9.2
Copeland | 3DB3A100L-TFD |  | 100 | 15 | 85 | 9.9
Copeland | 3DB3A100L-TFD |  | 100 | 20 | 80 | 10.7
Copeland | 3DB3A100L-TFD |  | 100 | 25 | 75 | 11.6
Copeland | 3DB3A100L-TFD |  | 100 | 30 | 70 | 12.5
Copeland | 3DB3A100L-TFD |  | 100 | 35 | 65 | 13.6
Copeland | 3DB3A100L-TFD |  | 90 | 10 | 80 | 10.7
Copeland | 3DB3A100L-TFD |  | 90 | 15 | 75 | 11.6
Copeland | 3DB3A100L-TFD |  | 90 | 20 | 70 | 12.6
Copeland | 3DB3A100L-TFD |  | 90 | 25 | 65 | 13.7
Copeland | 3DB3A100L-TFD |  | 90 | 30 | 60 | 15
Copeland | 3DB3A100L-TFD |  | 90 | 35 | 55 | 16.4
Copeland | 3DB3A100L-TFD |  | 70 | 10 | 60 | 14.6
Copeland | 3DB3A100L-TFD |  | 70 | 15 | 55 | 16.1
Copeland | 3DB3A100L-TFD |  | 70 | 20 | 50 | 17.8
Copeland | 3DB3A100L-TFD |  | 70 | 25 | 45 | 19.7
Copeland | 3DB3A100L-TFD |  | 70 | 30 | 40 | 21.9
Copeland | 3DB3A100L-TFD |  | 70 | 35 | 35 | 24.4
Copeland | 3DS3A150E-TFD |  | 110 | 10 | 100 | 7.8
Copeland | 3DS3A150E-TFD |  | 110 | 15 | 95 | 8.3
Copeland | 3DS3A150E-TFD |  | 110 | 20 | 90 | 8.9
Copeland | 3DS3A150E-TFD |  | 110 | 25 | 85 | 9.6
Copeland | 3DS3A150E-TFD |  | 110 | 30 | 80 | 10.3
Copeland | 3DS3A150E-TFD |  | 110 | 35 | 75 | 11
Copeland | 3DS3A150E-TFD |  | 100 | 10 | 90 | 9.1
Copeland | 3DS3A150E-TFD |  | 100 | 15 | 85 | 9.7
Copeland | 3DS3A150E-TFD |  | 100 | 20 | 80 | 10.5
Copeland | 3DS3A150E-TFD |  | 100 | 25 | 75 | 11.3
Copeland | 3DS3A150E-TFD |  | 100 | 30 | 70 | 12.2
Copeland | 3DS3A150E-TFD |  | 100 | 35 | 65 | 13.2
Copeland | 3DS3A150E-TFD |  | 90 | 10 | 80 | 10.5
Copeland | 3DS3A150E-TFD |  | 90 | 15 | 75 | 11.4
Copeland | 3DS3A150E-TFD |  | 90 | 20 | 70 | 12.4
Copeland | 3DS3A150E-TFD |  | 90 | 25 | 65 | 13.4
Copeland | 3DS3A150E-TFD |  | 90 | 30 | 60 | 14.6
Copeland | 3DS3A150E-TFD |  | 90 | 35 | 55 | 15.9
Copeland | 3DS3A150E-TFD |  | 70 | 10 | 60 | 14.5
Copeland | 3DS3A150E-TFD |  | 70 | 15 | 55 | 15.9
Copeland | 3DS3A150E-TFD |  | 70 | 20 | 50 | 17.5
Copeland | 3DS3A150E-TFD |  | 70 | 25 | 45 | 19.3
Copeland | 3DS3A150E-TFD |  | 70 | 30 | 40 | 21.4
Copeland | 3DS3A150E-TFD |  | 70 | 35 | 35 | 23.8
Copeland | 4DA3R18ME-TSK |  | 110 | 10 | 100 | 7.8
Copeland | 4DA3R18ME-TSK |  | 110 | 15 | 95 | 8.5
Copeland | 4DA3R18ME-TSK |  | 110 | 20 | 90 | 9.2
Copeland | 4DA3R18ME-TSK |  | 110 | 25 | 85 | 9.9
Copeland | 4DA3R18ME-TSK |  | 110 | 30 | 80 | 10.7
Copeland | 4DA3R18ME-TSK |  | 110 | 35 | 75 | 11.6
Copeland | 4DA3R18ME-TSK |  | 100 | 10 | 90 | 9.3
Copeland | 4DA3R18ME-TSK |  | 100 | 15 | 85 | 10.1
Copeland | 4DA3R18ME-TSK |  | 100 | 20 | 80 | 11
Copeland | 4DA3R18ME-TSK |  | 100 | 25 | 75 | 11.9
Copeland | 4DA3R18ME-TSK |  | 100 | 30 | 70 | 13
Copeland | 4DA3R18ME-TSK |  | 100 | 35 | 65 | 14.1
Copeland | 4DA3R18ME-TSK |  | 90 | 10 | 80 | 11
Copeland | 4DA3R18ME-TSK |  | 90 | 15 | 75 | 12
Copeland | 4DA3R18ME-TSK |  | 90 | 20 | 70 | 13.1
Copeland | 4DA3R18ME-TSK |  | 90 | 25 | 65 | 14.3
Copeland | 4DA3R18ME-TSK |  | 90 | 30 | 60 | 15.7
Copeland | 4DA3R18ME-TSK |  | 90 | 35 | 55 | 17.1
Copeland | 4DA3R18ME-TSK |  | 70 | 10 | 60 | 15.3
Copeland | 4DA3R18ME-TSK |  | 70 | 15 | 55 | 17
Copeland | 4DA3R18ME-TSK |  | 70 | 20 | 50 | 18.9
Copeland | 4DA3R18ME-TSK |  | 70 | 25 | 45 | 21.1
Copeland | 4DA3R18ME-TSK |  | 70 | 30 | 40 | 23.6
Copeland | 4DA3R18ME-TSK |  | 70 | 35 | 35 | 26.5
Copeland | 3DS3A150L-TFD |  | 110 | 10 | 100 | 7.8
Copeland | 3DS3A150L-TFD |  | 110 | 15 | 95 | 8.3
Copeland | 3DS3A150L-TFD |  | 110 | 20 | 90 | 8.9
Copeland | 3DS3A150L-TFD |  | 110 | 25 | 85 | 9.6
Copeland | 3DS3A150L-TFD |  | 110 | 30 | 80 | 10.3
Copeland | 3DS3A150L-TFD |  | 110 | 35 | 75 | 11
Copeland | 3DS3A150L-TFD |  | 100 | 10 | 90 | 9.1
Copeland | 3DS3A150L-TFD |  | 100 | 15 | 85 | 9.7
Copeland | 3DS3A150L-TFD |  | 100 | 20 | 80 | 10.5
Copeland | 3DS3A150L-TFD |  | 100 | 25 | 75 | 11.3
Copeland | 3DS3A150L-TFD |  | 100 | 30 | 70 | 12.2
Copeland | 3DS3A150L-TFD |  | 100 | 35 | 65 | 13.2
Copeland | 3DS3A150L-TFD |  | 90 | 10 | 80 | 10.5
Copeland | 3DS3A150L-TFD |  | 90 | 15 | 75 | 11.4
Copeland | 3DS3A150L-TFD |  | 90 | 20 | 70 | 12.4
Copeland | 3DS3A150L-TFD |  | 90 | 25 | 65 | 13.4
Copeland | 3DS3A150L-TFD |  | 90 | 30 | 60 | 14.6
Copeland | 3DS3A150L-TFD |  | 90 | 35 | 55 | 15.9
Copeland | 3DS3A150L-TFD |  | 70 | 10 | 60 | 14.5
Copeland | 3DS3A150L-TFD |  | 70 | 15 | 55 | 15.9
Copeland | 3DS3A150L-TFD |  | 70 | 20 | 50 | 17.5
Copeland | 3DS3A150L-TFD |  | 70 | 25 | 45 | 19.3
Copeland | 3DS3A150L-TFD |  | 70 | 30 | 40 | 21.4
Copeland | 3DS3A150L-TFD |  | 70 | 35 | 35 | 23.8
Copeland | 4DH3R22ME-TSK |  | 110 | 10 | 100 | 7.8
Copeland | 4DH3R22ME-TSK |  | 110 | 15 | 95 | 8.4
Copeland | 4DH3R22ME-TSK |  | 110 | 20 | 90 | 9
Copeland | 4DH3R22ME-TSK |  | 110 | 25 | 85 | 9.7
Copeland | 4DH3R22ME-TSK |  | 110 | 30 | 80 | 10.4
Copeland | 4DH3R22ME-TSK |  | 110 | 35 | 75 | 11.1
Copeland | 4DH3R22ME-TSK |  | 100 | 10 | 90 | 9.1
Copeland | 4DH3R22ME-TSK |  | 100 | 15 | 85 | 9.9
Copeland | 4DH3R22ME-TSK |  | 100 | 20 | 80 | 10.7
Copeland | 4DH3R22ME-TSK |  | 100 | 25 | 75 | 11.5
Copeland | 4DH3R22ME-TSK |  | 100 | 30 | 70 | 12.4
Copeland | 4DH3R22ME-TSK |  | 100 | 35 | 65 | 13.4
Copeland | 4DH3R22ME-TSK |  | 90 | 10 | 80 | 10.8
Copeland | 4DH3R22ME-TSK |  | 90 | 15 | 75 | 11.7
Copeland | 4DH3R22ME-TSK |  | 90 | 20 | 70 | 12.7
Copeland | 4DH3R22ME-TSK |  | 90 | 25 | 65 | 13.8
Copeland | 4DH3R22ME-TSK |  | 90 | 30 | 60 | 15
Copeland | 4DH3R22ME-TSK |  | 90 | 35 | 55 | 16.3
Copeland | 4DH3R22ME-TSK |  | 70 | 10 | 60 | 15.3
Copeland | 4DH3R22ME-TSK |  | 70 | 15 | 55 | 16.9
Copeland | 4DH3R22ME-TSK |  | 70 | 20 | 50 | 18.7
Copeland | 4DH3R22ME-TSK |  | 70 | 25 | 45 | 20.6
Copeland | 4DH3R22ME-TSK |  | 70 | 30 | 40 | 22.9
Copeland | 4DH3R22ME-TSK |  | 70 | 35 | 35 | 25.4
Copeland | 3DB3R12ME-TFD |  | 110 | 10 | 100 | 7.9
Copeland | 3DB3R12ME-TFD |  | 110 | 15 | 95 | 8.4
Copeland | 3DB3R12ME-TFD |  | 110 | 20 | 90 | 9.1
Copeland | 3DB3R12ME-TFD |  | 110 | 25 | 85 | 9.8
Copeland | 3DB3R12ME-TFD |  | 110 | 30 | 80 | 10.5
Copeland | 3DB3R12ME-TFD |  | 110 | 35 | 75 | 11.4
Copeland | 3DB3R12ME-TFD |  | 100 | 10 | 90 | 9.2
Copeland | 3DB3R12ME-TFD |  | 100 | 15 | 85 | 9.9
Copeland | 3DB3R12ME-TFD |  | 100 | 20 | 80 | 10.7
Copeland | 3DB3R12ME-TFD |  | 100 | 25 | 75 | 11.6
Copeland | 3DB3R12ME-TFD |  | 100 | 30 | 70 | 12.5
Copeland | 3DB3R12ME-TFD |  | 100 | 35 | 65 | 13.6
Copeland | 3DB3R12ME-TFD |  | 90 | 10 | 80 | 10.7
Copeland | 3DB3R12ME-TFD |  | 90 | 15 | 75 | 11.6
Copeland | 3DB3R12ME-TFD |  | 90 | 20 | 70 | 12.6
Copeland | 3DB3R12ME-TFD |  | 90 | 25 | 65 | 13.7
Copeland | 3DB3R12ME-TFD |  | 90 | 30 | 60 | 15
Copeland | 3DB3R12ME-TFD |  | 90 | 35 | 55 | 16.4
Copeland | 3DB3R12ME-TFD |  | 70 | 10 | 60 | 14.6
Copeland | 3DB3R12ME-TFD |  | 70 | 15 | 55 | 16.1
Copeland | 3DB3R12ME-TFD |  | 70 | 20 | 50 | 17.8
Copeland | 3DB3R12ME-TFD |  | 70 | 25 | 45 | 19.7
Copeland | 3DB3R12ME-TFD |  | 70 | 30 | 40 | 21.9
Copeland | 3DB3R12ME-TFD |  | 70 | 35 | 35 | 24.4
Copeland | 3DA3F28KL-TFD |  | 110 | -30 | 140 | 4.6
Copeland | 3DA3F28KL-TFD |  | 110 | -25 | 135 | 4.9
Copeland | 3DA3F28KL-TFD |  | 110 | -20 | 130 | 5.3
Copeland | 3DA3F28KL-TFD |  | 110 | -15 | 125 | 5.6
Copeland | 3DA3F28KL-TFD |  | 110 | -10 | 120 | 6
Copeland | 3DA3F28KL-TFD |  | 110 | -5 | 115 | 6.5
Copeland | 3DA3F28KL-TFD |  | 105 | -30 | 135 | 4.9
Copeland | 3DA3F28KL-TFD |  | 105 | -25 | 130 | 5.2
Copeland | 3DA3F28KL-TFD |  | 105 | -20 | 125 | 5.6
Copeland | 3DA3F28KL-TFD |  | 105 | -15 | 120 | 6
Copeland | 3DA3F28KL-TFD |  | 105 | -10 | 115 | 6.5
Copeland | 3DA3F28KL-TFD |  | 105 | -5 | 110 | 7
Copeland | 3DA3F28KL-TFD |  | 100 | -30 | 130 | 5.2
Copeland | 3DA3F28KL-TFD |  | 100 | -25 | 125 | 5.6
Copeland | 3DA3F28KL-TFD |  | 100 | -20 | 120 | 6
Copeland | 3DA3F28KL-TFD |  | 100 | -15 | 115 | 6.5
Copeland | 3DA3F28KL-TFD |  | 100 | -10 | 110 | 7
Copeland | 3DA3F28KL-TFD |  | 100 | -5 | 105 | 7.5
Copeland | 3DA3F28KL-TFD |  | 80 | -30 | 110 | 6.6
Copeland | 3DA3F28KL-TFD |  | 80 | -25 | 105 | 7.2
Copeland | 3DA3F28KL-TFD |  | 80 | -20 | 100 | 7.8
Copeland | 3DA3F28KL-TFD |  | 80 | -15 | 95 | 8.5
Copeland | 3DA3F28KL-TFD |  | 80 | -10 | 90 | 9.2
Copeland | 3DA3F28KL-TFD |  | 80 | -5 | 85 | 10
Copeland | 3DA3F28KL-TFD |  | 70 | -30 | 100 | 7.5
Copeland | 3DA3F28KL-TFD |  | 70 | -25 | 95 | 8.2
Copeland | 3DA3F28KL-TFD |  | 70 | -20 | 90 | 8.9
Copeland | 3DA3F28KL-TFD |  | 70 | -15 | 85 | 9.7
Copeland | 3DA3F28KL-TFD |  | 70 | -10 | 80 | 10.5
Copeland | 3DA3F28KL-TFD |  | 70 | -5 | 75 | 11.3
Copeland | 3DF3F40KL-TFD |  | 110 | -30 | 140 | 4.7
Copeland | 3DF3F40KL-TFD |  | 110 | -25 | 135 | 5
Copeland | 3DF3F40KL-TFD |  | 110 | -20 | 130 | 5.3
Copeland | 3DF3F40KL-TFD |  | 110 | -15 | 125 | 5.7
Copeland | 3DF3F40KL-TFD |  | 110 | -10 | 120 | 6
Copeland | 3DF3F40KL-TFD |  | 110 | -5 | 115 | 6.4
Copeland | 3DF3F40KL-TFD |  | 105 | -30 | 135 | 5
Copeland | 3DF3F40KL-TFD |  | 105 | -25 | 130 | 5.3
Copeland | 3DF3F40KL-TFD |  | 105 | -20 | 125 | 5.7
Copeland | 3DF3F40KL-TFD |  | 105 | -15 | 120 | 6.1
Copeland | 3DF3F40KL-TFD |  | 105 | -10 | 115 | 6.5
Copeland | 3DF3F40KL-TFD |  | 105 | -5 | 110 | 6.9
Copeland | 3DF3F40KL-TFD |  | 100 | -30 | 130 | 5.3
Copeland | 3DF3F40KL-TFD |  | 100 | -25 | 125 | 5.7
Copeland | 3DF3F40KL-TFD |  | 100 | -20 | 120 | 6
Copeland | 3DF3F40KL-TFD |  | 100 | -15 | 115 | 6.5
Copeland | 3DF3F40KL-TFD |  | 100 | -10 | 110 | 6.9
Copeland | 3DF3F40KL-TFD |  | 100 | -5 | 105 | 7.4
Copeland | 3DF3F40KL-TFD |  | 80 | -30 | 110 | 6.7
Copeland | 3DF3F40KL-TFD |  | 80 | -25 | 105 | 7.3
Copeland | 3DF3F40KL-TFD |  | 80 | -20 | 100 | 7.8
Copeland | 3DF3F40KL-TFD |  | 80 | -15 | 95 | 8.4
Copeland | 3DF3F40KL-TFD |  | 80 | -10 | 90 | 9.1
Copeland | 3DF3F40KL-TFD |  | 80 | -5 | 85 | 9.8
Copeland | 3DF3F40KL-TFD |  | 70 | -30 | 100 | 7.6
Copeland | 3DF3F40KL-TFD |  | 70 | -25 | 95 | 8.2
Copeland | 3DF3F40KL-TFD |  | 70 | -20 | 90 | 8.9
Copeland | 3DF3F40KL-TFD |  | 70 | -15 | 85 | 9.6
Copeland | 3DF3F40KL-TFD |  | 70 | -10 | 80 | 10.4
Copeland | 3DF3F40KL-TFD |  | 70 | -5 | 75 | 11.2
Copeland | 2DL3R78KL-TFD |  | 110 | 10 | 100 | 8
Copeland | 2DL3R78KL-TFD |  | 110 | 15 | 95 | 8.6
Copeland | 2DL3R78KL-TFD |  | 110 | 20 | 90 | 9.3
Copeland | 2DL3R78KL-TFD |  | 110 | 25 | 85 | 10
Copeland | 2DL3R78KL-TFD |  | 110 | 30 | 80 | 10.8
Copeland | 2DL3R78KL-TFD |  | 110 | 35 | 75 | 11.7
Copeland | 2DL3R78KL-TFD |  | 100 | 10 | 90 | 9.3
Copeland | 2DL3R78KL-TFD |  | 100 | 15 | 85 | 10.1
Copeland | 2DL3R78KL-TFD |  | 100 | 20 | 80 | 10.9
Copeland | 2DL3R78KL-TFD |  | 100 | 25 | 75 | 11.9
Copeland | 2DL3R78KL-TFD |  | 100 | 30 | 70 | 12.9
Copeland | 2DL3R78KL-TFD |  | 100 | 35 | 65 | 14.1
Copeland | 2DL3R78KL-TFD |  | 90 | 10 | 80 | 10.9
Copeland | 2DL3R78KL-TFD |  | 90 | 15 | 75 | 11.9
Copeland | 2DL3R78KL-TFD |  | 90 | 20 | 70 | 12.9
Copeland | 2DL3R78KL-TFD |  | 90 | 25 | 65 | 14.1
Copeland | 2DL3R78KL-TFD |  | 90 | 30 | 60 | 15.5
Copeland | 2DL3R78KL-TFD |  | 90 | 35 | 55 | 17
Copeland | 2DL3R78KL-TFD |  | 70 | 10 | 60 | 15.2
Copeland | 2DL3R78KL-TFD |  | 70 | 15 | 55 | 16.8
Copeland | 2DL3R78KL-TFD |  | 70 | 20 | 50 | 18.6
Copeland | 2DL3R78KL-TFD |  | 70 | 25 | 45 | 20.7
Copeland | 2DL3R78KL-TFD |  | 70 | 30 | 40 | 23.1
Copeland | 2DL3R78KL-TFD |  | 70 | 35 | 35 | 26
Copeland | 3DF3R15ML-TFD |  | 110 | 10 | 100 | 7.8
Copeland | 3DF3R15ML-TFD |  | 110 | 15 | 95 | 8.3
Copeland | 3DF3R15ML-TFD |  | 110 | 20 | 90 | 8.9
Copeland | 3DF3R15ML-TFD |  | 110 | 25 | 85 | 9.6
Copeland | 3DF3R15ML-TFD |  | 110 | 30 | 80 | 10.3
Copeland | 3DF3R15ML-TFD |  | 110 | 35 | 75 | 11
Copeland | 3DF3R15ML-TFD |  | 100 | 10 | 90 | 9.1
Copeland | 3DF3R15ML-TFD |  | 100 | 15 | 85 | 9.7
Copeland | 3DF3R15ML-TFD |  | 100 | 20 | 80 | 10.5
Copeland | 3DF3R15ML-TFD |  | 100 | 25 | 75 | 11.3
Copeland | 3DF3R15ML-TFD |  | 100 | 30 | 70 | 12.2
Copeland | 3DF3R15ML-TFD |  | 100 | 35 | 65 | 13.2
Copeland | 3DF3R15ML-TFD |  | 90 | 10 | 80 | 10.5
Copeland | 3DF3R15ML-TFD |  | 90 | 15 | 75 | 11.4
Copeland | 3DF3R15ML-TFD |  | 90 | 20 | 70 | 12.4
Copeland | 3DF3R15ML-TFD |  | 90 | 25 | 65 | 13.4
Copeland | 3DF3R15ML-TFD |  | 90 | 30 | 60 | 14.6
Copeland | 3DF3R15ML-TFD |  | 90 | 35 | 55 | 15.9
Copeland | 3DF3R15ML-TFD |  | 70 | 10 | 60 | 14.5
Copeland | 3DF3R15ML-TFD |  | 70 | 15 | 55 | 15.9
Copeland | 3DF3R15ML-TFD |  | 70 | 20 | 50 | 17.5
Copeland | 3DF3R15ML-TFD |  | 70 | 25 | 45 | 19.3
Copeland | 3DF3R15ML-TFD |  | 70 | 30 | 40 | 21.4
Copeland | 3DF3R15ML-TFD |  | 70 | 35 | 35 | 23.8
Copeland | 2DB3F25KL-TFD |  | 110 | -30 | 140 | 4.6
Copeland | 2DB3F25KL-TFD |  | 110 | -25 | 135 | 5
Copeland | 2DB3F25KL-TFD |  | 110 | -20 | 130 | 5.4
Copeland | 2DB3F25KL-TFD |  | 110 | -15 | 125 | 5.7
Copeland | 2DB3F25KL-TFD |  | 110 | -10 | 120 | 6.2
Copeland | 2DB3F25KL-TFD |  | 110 | -5 | 115 | 6.6
Copeland | 2DB3F25KL-TFD |  | 105 | -30 | 135 | 4.9
Copeland | 2DB3F25KL-TFD |  | 105 | -25 | 130 | 5.3
Copeland | 2DB3F25KL-TFD |  | 105 | -20 | 125 | 5.7
Copeland | 2DB3F25KL-TFD |  | 105 | -15 | 120 | 6.2
Copeland | 2DB3F25KL-TFD |  | 105 | -10 | 115 | 6.6
Copeland | 2DB3F25KL-TFD |  | 105 | -5 | 110 | 7.1
Copeland | 2DB3F25KL-TFD |  | 100 | -30 | 130 | 5.3
Copeland | 2DB3F25KL-TFD |  | 100 | -25 | 125 | 5.7
Copeland | 2DB3F25KL-TFD |  | 100 | -20 | 120 | 6.1
Copeland | 2DB3F25KL-TFD |  | 100 | -15 | 115 | 6.6
Copeland | 2DB3F25KL-TFD |  | 100 | -10 | 110 | 7.1
Copeland | 2DB3F25KL-TFD |  | 100 | -5 | 105 | 7.6
Copeland | 2DB3F25KL-TFD |  | 80 | -30 | 110 | 6.8
Copeland | 2DB3F25KL-TFD |  | 80 | -25 | 105 | 7.4
Copeland | 2DB3F25KL-TFD |  | 80 | -20 | 100 | 8
Copeland | 2DB3F25KL-TFD |  | 80 | -15 | 95 | 8.7
Copeland | 2DB3F25KL-TFD |  | 80 | -10 | 90 | 9.4
Copeland | 2DB3F25KL-TFD |  | 80 | -5 | 85 | 10.2
Copeland | 2DB3F25KL-TFD |  | 70 | -30 | 100 | 7.8
Copeland | 2DB3F25KL-TFD |  | 70 | -25 | 95 | 8.5
Copeland | 2DB3F25KL-TFD |  | 70 | -20 | 90 | 9.2
Copeland | 2DB3F25KL-TFD |  | 70 | -15 | 85 | 10
Copeland | 2DB3F25KL-TFD |  | 70 | -10 | 80 | 10.9
Copeland | 2DB3F25KL-TFD |  | 70 | -5 | 75 | 11.8
Copeland | 2DL3F20KL-TFD |  | 110 | -30 | 140 | 4.5
Copeland | 2DL3F20KL-TFD |  | 110 | -25 | 135 | 4.9
Copeland | 2DL3F20KL-TFD |  | 110 | -20 | 130 | 5.3
Copeland | 2DL3F20KL-TFD |  | 110 | -15 | 125 | 5.6
Copeland | 2DL3F20KL-TFD |  | 110 | -10 | 120 | 6.1
Copeland | 2DL3F20KL-TFD |  | 110 | -5 | 115 | 6.5
Copeland | 2DL3F20KL-TFD |  | 105 | -30 | 135 | 4.9
Copeland | 2DL3F20KL-TFD |  | 105 | -25 | 130 | 5.2
Copeland | 2DL3F20KL-TFD |  | 105 | -20 | 125 | 5.6
Copeland | 2DL3F20KL-TFD |  | 105 | -15 | 120 | 6.1
Copeland | 2DL3F20KL-TFD |  | 105 | -10 | 115 | 6.5
Copeland | 2DL3F20KL-TFD |  | 105 | -5 | 110 | 7
Copeland | 2DL3F20KL-TFD |  | 100 | -30 | 130 | 5.2
Copeland | 2DL3F20KL-TFD |  | 100 | -25 | 125 | 5.6
Copeland | 2DL3F20KL-TFD |  | 100 | -20 | 120 | 6
Copeland | 2DL3F20KL-TFD |  | 100 | -15 | 115 | 6.5
Copeland | 2DL3F20KL-TFD |  | 100 | -10 | 110 | 7
Copeland | 2DL3F20KL-TFD |  | 100 | -5 | 105 | 7.5
Copeland | 2DL3F20KL-TFD |  | 80 | -30 | 110 | 6.7
Copeland | 2DL3F20KL-TFD |  | 80 | -25 | 105 | 7.3
Copeland | 2DL3F20KL-TFD |  | 80 | -20 | 100 | 7.9
Copeland | 2DL3F20KL-TFD |  | 80 | -15 | 95 | 8.6
Copeland | 2DL3F20KL-TFD |  | 80 | -10 | 90 | 9.3
Copeland | 2DL3F20KL-TFD |  | 80 | -5 | 85 | 10
Copeland | 2DL3F20KL-TFD |  | 70 | -30 | 100 | 7.6
Copeland | 2DL3F20KL-TFD |  | 70 | -25 | 95 | 8.3
Copeland | 2DL3F20KL-TFD |  | 70 | -20 | 90 | 9
Copeland | 2DL3F20KL-TFD |  | 70 | -15 | 85 | 9.8
Copeland | 2DL3F20KL-TFD |  | 70 | -10 | 80 | 10.7
Copeland | 2DL3F20KL-TFD |  | 70 | -5 | 75 | 11.6
Copeland | 3DB3R12ML-TFD |  | 110 | 10 | 100 | 7.9
Copeland | 3DB3R12ML-TFD |  | 110 | 15 | 95 | 8.4
Copeland | 3DB3R12ML-TFD |  | 110 | 20 | 90 | 9.1
Copeland | 3DB3R12ML-TFD |  | 110 | 25 | 85 | 9.8
Copeland | 3DB3R12ML-TFD |  | 110 | 30 | 80 | 10.5
Copeland | 3DB3R12ML-TFD |  | 110 | 35 | 75 | 11.4
Copeland | 3DB3R12ML-TFD |  | 100 | 10 | 90 | 9.2
Copeland | 3DB3R12ML-TFD |  | 100 | 15 | 85 | 9.9
Copeland | 3DB3R12ML-TFD |  | 100 | 20 | 80 | 10.7
Copeland | 3DB3R12ML-TFD |  | 100 | 25 | 75 | 11.6
Copeland | 3DB3R12ML-TFD |  | 100 | 30 | 70 | 12.5
Copeland | 3DB3R12ML-TFD |  | 100 | 35 | 65 | 13.6
Copeland | 3DB3R12ML-TFD |  | 90 | 10 | 80 | 10.7
Copeland | 3DB3R12ML-TFD |  | 90 | 15 | 75 | 11.6
Copeland | 3DB3R12ML-TFD |  | 90 | 20 | 70 | 12.6
Copeland | 3DB3R12ML-TFD |  | 90 | 25 | 65 | 13.7
Copeland | 3DB3R12ML-TFD |  | 90 | 30 | 60 | 15
Copeland | 3DB3R12ML-TFD |  | 90 | 35 | 55 | 16.4
Copeland | 3DB3R12ML-TFD |  | 70 | 10 | 60 | 14.6
Copeland | 3DB3R12ML-TFD |  | 70 | 15 | 55 | 16.1
Copeland | 3DB3R12ML-TFD |  | 70 | 20 | 50 | 17.8
Copeland | 3DB3R12ML-TFD |  | 70 | 25 | 45 | 19.7
Copeland | 3DB3R12ML-TFD |  | 70 | 30 | 40 | 21.9
Copeland | 3DB3R12ML-TFD |  | 70 | 35 | 35 | 24.4
Bitzer | 2C0692SL-4SU | 3 | 90 | 20 | 70 | 12.2392
Bitzer | 2C0692SL-4SU | 3 | 90 | 15 | 75 | 11.3492
Bitzer | 2C0692SL-4SU | 3 | 90 | 5 | 85 | 9.7406
Bitzer | 2C0692SL-4SU | 3 | 90 | 0 | 90 | 9.0303
Bitzer | 2C0692SL-4SU | 3 | 90 | -5 | 95 | 8.3706
Bitzer | 2C0692SL-4SU | 3 | 90 | -10 | 100 | 7.7627
Bitzer | 2C0692SL-4SU | 3 | 90 | -20 | 110 | 6.6628
Bitzer | 2C0692SL-4SU | 3 | 90 | -25 | 115 | 6.1458
Bitzer | 2C0692SL-4SU | 3 | 90 | -30 | 120 | 5.7059
Bitzer | 2C0692SL-4SU | 3 | 110 | 20 | 90 | 8.6374
Bitzer | 2C0692SL-4SU | 3 | 110 | 15 | 95 | 8.0831
Bitzer | 2C0692SL-4SU | 3 | 110 | 5 | 105 | 7.0566
Bitzer | 2C0692SL-4SU | 3 | 110 | 0 | 110 | 6.5984
Bitzer | 2C0692SL-4SU | 3 | 110 | -5 | 115 | 6.1516
Bitzer | 2C0692SL-4SU | 3 | 110 | -10 | 120 | 5.7406
Bitzer | 2C0692SL-4SU | 3 | 110 | -20 | 130 | 4.9926
Bitzer | 2C0692SL-4SU | 3 | 110 | -25 | 135 | 4.6305
Bitzer | 2C0692SL-4SU | 3 | 110 | -30 | 140 | 4.3053
Bitzer | 4C0770SL-4SU | 3 | 90 | 20 | 70 | 11.652
Bitzer | 4C0770SL-4SU | 3 | 90 | 15 | 75 | 10.7763
Bitzer | 4C0770SL-4SU | 3 | 90 | 5 | 85 | 9.2308
Bitzer | 4C0770SL-4SU | 3 | 90 | 0 | 90 | 8.5547
Bitzer | 4C0770SL-4SU | 3 | 90 | -5 | 95 | 7.9258
Bitzer | 4C0770SL-4SU | 3 | 90 | -10 | 100 | 7.3615
Bitzer | 4C0770SL-4SU | 3 | 90 | -20 | 110 | 6.3167
Bitzer | 4C0770SL-4SU | 3 | 90 | -25 | 115 | 5.8489
Bitzer | 4C0770SL-4SU | 3 | 110 | 20 | 90 | 8.3333
Bitzer | 4C0770SL-4SU | 3 | 110 | 15 | 95 | 7.8093
Bitzer | 4C0770SL-4SU | 3 | 110 | 5 | 105 | 6.8213
Bitzer | 4C0770SL-4SU | 3 | 110 | 0 | 110 | 6.3702
Bitzer | 4C0770SL-4SU | 3 | 110 | -5 | 115 | 5.964
Bitzer | 4C0770SL-4SU | 3 | 110 | -10 | 120 | 5.5663
Bitzer | 4C0770SL-4SU | 3 | 110 | -20 | 130 | 4.8404
Bitzer | 4C0770SL-4SU | 3 | 110 | -25 | 135 | 4.5036
Bitzer | 4C2397SL-2NU | 12.5 | 90 | 20 | 70 | 11.7234
Bitzer | 4C2397SL-2NU | 12.5 | 90 | 15 | 75 | 10.9117
Bitzer | 4C2397SL-2NU | 12.5 | 90 | 5 | 85 | 9.498
Bitzer | 4C2397SL-2NU | 12.5 | 90 | 0 | 90 | 8.887
Bitzer | 4C2397SL-2NU | 12.5 | 90 | -5 | 95 | 8.3065
Bitzer | 4C2397SL-2NU | 12.5 | 90 | -10 | 100 | 7.7682
Bitzer | 4C2397SL-2NU | 12.5 | 90 | -20 | 110 | 6.7969
Bitzer | 4C2397SL-2NU | 12.5 | 90 | -25 | 115 | 6.3504
Bitzer | 4C2397SL-2NU | 12.5 | 90 | -30 | 120 | 5.9267
Bitzer | 4C2397SL-2NU | 12.5 | 110 | 20 | 90 | 8.5759
Bitzer | 4C2397SL-2NU | 12.5 | 110 | 15 | 95 | 8.0561
Bitzer | 4C2397SL-2NU | 12.5 | 110 | 5 | 105 | 7.1145
Bitzer | 4C2397SL-2NU | 12.5 | 110 | 0 | 110 | 6.7007
Bitzer | 4C2397SL-2NU | 12.5 | 110 | -5 | 115 | 6.306
Bitzer | 4C2397SL-2NU | 12.5 | 110 | -10 | 120 | 5.9286
Bitzer | 4C2397SL-2NU | 12.5 | 110 | -20 | 130 | 5.2355
Bitzer | 4C2397SL-2NU | 12.5 | 110 | -25 | 135 | 4.903
Bitzer | 4C2397SL-2NU | 12.5 | 110 | -30 | 140 | 4.5873
Bitzer | 4C0969SL-4SU | 4 | 90 | 20 | 70 | 12.2426
Bitzer | 4C0969SL-4SU | 4 | 90 | 15 | 75 | 11.3143
Bitzer | 4C0969SL-4SU | 4 | 90 | 5 | 85 | 9.6694
Bitzer | 4C0969SL-4SU | 4 | 90 | 0 | 90 | 8.9674
Bitzer | 4C0969SL-4SU | 4 | 90 | -5 | 95 | 8.3028
Bitzer | 4C0969SL-4SU | 4 | 90 | -10 | 100 | 7.7195
Bitzer | 4C0969SL-4SU | 4 | 90 | -20 | 110 | 6.6387
Bitzer | 4C0969SL-4SU | 4 | 90 | -25 | 115 | 6.1702
Bitzer | 4C0969SL-4SU | 4 | 90 | -30 | 120 | 5.7351
Bitzer | 4C0969SL-4SU | 4 | 110 | 20 | 90 | 8.6634
Bitzer | 4C0969SL-4SU | 4 | 110 | 15 | 95 | 8.0776
Bitzer | 4C0969SL-4SU | 4 | 110 | 5 | 105 | 7.0263
Bitzer | 4C0969SL-4SU | 4 | 110 | 0 | 110 | 6.5669
Bitzer | 4C0969SL-4SU | 4 | 110 | -5 | 115 | 6.1301
Bitzer | 4C0969SL-4SU | 4 | 110 | -10 | 120 | 5.7339
Bitzer | 4C0969SL-4SU | 4 | 110 | -20 | 130 | 4.9837
Bitzer | 4C0969SL-4SU | 4 | 110 | -25 | 135 | 4.6507
Bitzer | 4C0969SL-4SU | 4 | 110 | -30 | 140 | 4.3411
Bitzer | 4C1761SL-2NU | 7.5 | 90 | 20 | 70 | 11.9565
Bitzer | 4C1761SL-2NU | 7.5 | 90 | 15 | 75 | 11.1649
Bitzer | 4C1761SL-2NU | 7.5 | 90 | 5 | 85 | 9.728
Bitzer | 4C1761SL-2NU | 7.5 | 90 | 0 | 90 | 9.092
Bitzer | 4C1761SL-2NU | 7.5 | 90 | -5 | 95 | 8.4878
Bitzer | 4C1761SL-2NU | 7.5 | 90 | -10 | 100 | 7.9194
Bitzer | 4C1761SL-2NU | 7.5 | 90 | -20 | 110 | 6.8976
Bitzer | 4C1761SL-2NU | 7.5 | 90 | -25 | 115 | 6.4321
Bitzer | 4C1761SL-2NU | 7.5 | 90 | -30 | 120 | 5.9839
Bitzer | 4C1761SL-2NU | 7.5 | 110 | 20 | 90 | 8.6521
Bitzer | 4C1761SL-2NU | 7.5 | 110 | 15 | 95 | 8.1422
Bitzer | 4C1761SL-2NU | 7.5 | 110 | 5 | 105 | 7.2
Bitzer | 4C1761SL-2NU | 7.5 | 110 | 0 | 110 | 6.7556
Bitzer | 4C1761SL-2NU | 7.5 | 110 | -5 | 115 | 6.3387
Bitzer | 4C1761SL-2NU | 7.5 | 110 | -10 | 120 | 5.9433
Bitzer | 4C1761SL-2NU | 7.5 | 110 | -20 | 130 | 5.1974
Bitzer | 4C1761SL-2NU | 7.5 | 110 | -25 | 135 | 4.847
Bitzer | 4C1761SL-2NU | 7.5 | 110 | -30 | 140 | 4.5251
Bitzer | 4B2707PL-2NU | 13 | 90 | 20 | 70 | 11.9751
Bitzer | 4B2707PL-2NU | 13 | 90 | 15 | 75 | 11.1392
Bitzer | 4B2707PL-2NU | 13 | 90 | 5 | 85 | 9.6811
Bitzer | 4B2707PL-2NU | 13 | 90 | 0 | 90 | 9.0366
Bitzer | 4B2707PL-2NU | 13 | 90 | -5 | 95 | 8.4415
Bitzer | 4B2707PL-2NU | 13 | 90 | -10 | 100 | 7.8921
Bitzer | 4B2707PL-2NU | 13 | 90 | -20 | 110 | 6.9141
Bitzer | 4B2707PL-2NU | 13 | 90 | -25 | 115 | 6.465
Bitzer | 4B2707PL-2NU | 13 | 90 | -30 | 120 | 6.0301
Bitzer | 4B2707PL-2NU | 13 | 110 | 20 | 90 | 8.6359
Bitzer | 4B2707PL-2NU | 13 | 110 | 15 | 95 | 8.1015
Bitzer | 4B2707PL-2NU | 13 | 110 | 5 | 105 | 7.1374
Bitzer | 4B2707PL-2NU | 13 | 110 | 0 | 110 | 6.705
Bitzer | 4B2707PL-2NU | 13 | 110 | -5 | 115 | 6.307
Bitzer | 4B2707PL-2NU | 13 | 110 | -10 | 120 | 5.9314
Bitzer | 4B2707PL-2NU | 13 | 110 | -20 | 130 | 5.2447
Bitzer | 4B2707PL-2NU | 13 | 110 | -25 | 135 | 4.9339
Bitzer | 4B2707PL-2NU | 13 | 110 | -30 | 140 | 4.6388